133776 | 5 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-06-01T00:00:00 | 2026-09-30T00:00:00 | 2026-10-21T00:00:00 | 2 | 0 | 2 | 11615.55 | 23231.1 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CB12L6221CY00U | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 2 - 27kV@25kA, Compartment Position: L - Lower, Bushing Type: 6 - Porcelain - 27kV 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 2 - Lexan, TOC Harness: 1 - 8 Contacts, Door Type: C - ODNWI Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 2 - 27kV@25kA, Compartment Position: L - Lower, Bushing Type: 6 - Porcelain - 27kV 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 2 - Lexan, TOC Harness: 1 - 8 Contacts, Door Type: C - ODNWI Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
133776 | 8 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-06-01T00:00:00 | 2026-10-28T00:00:00 | 2026-10-28T00:00:00 | 2 | 0 | 2 | 5622.96 | 11245.92 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CPTB951513200D151 | Control Power Transformer: 95 kV BIL, 15 kVA, 15 kV NSV, Primary voltage: 13200, Secondary voltage, 120/240 | PUR | Control Power Transformer: 95 kV BIL, 15 kVA, 15 kV NSV, Primary voltage: 13200, Secondary voltage, 120/240 | EA | EA |  | TRUE |  | P | B/W | DAYTON
129578 | 17 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2025-10-24T00:00:00 | 2026-12-01T00:00:00 | 2026-09-28T00:00:00 | 2 | 0 | 2 | 8900 | 17800 | 66061 | USA | N45 | 1524 | ABB INC | 27511 | FSULITHI136X8P1 | Level-3 Startup of Lithium-Ion Batteries Note: Installation & connecting of batteries in the cabinets are by others (per adder above) |  | Level-3 Startup of Lithium-Ion BatteriesNote: Installation & connecting of batteries in the cabinets are by others | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077178-3-1
129578 | 18 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2025-10-24T00:00:00 | 2026-12-01T00:00:00 | 2026-09-28T00:00:00 | 1 | 0 | 1 | 13350 | 13350 | 66061 | USA | N45 | 1524 | ABB INC | 27511 | S-CM1_UPS | (Customer to decide) Spec 263353, Par 3.5.D Level-4 Performance Testing per system Par 3.5.D: Exploratory period - 1st 2 days onsite Note: Customer to decide if this step is necessary |  | Spec 263353, Par 3.5 Level-4 Performance Testing for BOTH systemPar 3.5.B: 2 days onsite + 1 day mobilization | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077178-3-1
129578 | 16 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2025-10-24T00:00:00 | 2026-12-01T00:00:00 | 2026-09-28T00:00:00 | 1 | 0 | 1 | 4450 | 4450 | 66061 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE | Level-3 Startup: Additional startup time - interfacing with and checking of Maintenance Bypass Switchboards (not actual SU of MBC or MBS) |  | Level-3 Startup: Additional startup time - interfacing with and checking of Maintenance Bypass Switchboards (not actual SU of MBC or MBS) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077178-3-1
129578 | 19 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2025-10-24T00:00:00 | 2026-12-01T00:00:00 | 2026-09-28T00:00:00 | 1 | 0 | 1 | 4450 | 4450 | 66061 | USA | N45 | 1524 | ABB INC | 27511 | S-CM1_UPS | (Customer to decide) Spec 263353, Par 3.5.D Level-4 Performance Testing per system Par 3.5.D: Exploratory period - 1st 2 days onsite Note: Customer to decide if this step is necessary |  | Spec 263353, Par 3.6A Level-5 Integration System Testing (IST)(1 day included + daily rate applied if exceeds) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077178-3-1
129578 | 14 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2025-10-24T00:00:00 | 2026-12-01T00:00:00 | 2026-09-28T00:00:00 | 1 | 0 | 1 | 4450 | 4450 | 66061 | USA | N45 | 1524 | ABB INC | 27511 | MOBILIZATION_UPS | Mobilization for UPS Pkg (assume startup at same time for both UPS's) |  | Mobilization for UPS Pkg (assume startup at same time for both UPS's) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077178-3-1
129578 | 15 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2025-10-24T00:00:00 | 2029-12-31T00:00:00 | 2029-12-31T00:00:00 | 2 | 0 | 2 | 11060 | 22120 | 66061 | USA | N45 | 1524 | ABB INC | 27511 | FSUMEG1600P1 | Level-3 Startup of MegaFlex UPS |  | Level-3 Startup of MegaFlex UPS | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077178-3-1
129578 | 20 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2025-10-24T00:00:00 | 2026-12-01T00:00:00 | 2026-09-25T00:00:00 | 1 | 0 | 1 | 4450 | 4450 | 66061 | USA | N45 | 1524 | ABB INC | 27511 | S-OST | Par 3.4.K - Onsite Training after startup/commissioning completion, contiguous US only (1 day / site + daily rate applied if exceeds) |  | Par 3.7 - Onsite Training after startup/commissioning completion, contiguous US only(1 day / site + daily rate applied if exceeds) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077178-3-1
131834 | 5 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-17T00:00:00 | 2026-09-17T00:00:00 | 2026-09-17T00:00:00 | 1 | 0 | 1 | 2877 | 2877 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | 931868T01 | Breaker Lift Truck Assembly - manually operated | PUR | Breaker Lift Truck Assembly - manually operated | EA | EA |  | TRUE |  | P | B/W | DAYTON
132283 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-07T00:00:00 | 2026-12-22T00:00:00 | 2026-12-22T00:00:00 | 1 | 0 | 1 | 22200 | 22200 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | Level 4 & 5 Onsite testing for ABB UPS & STS | Category: --- Identifier: --- Level 4 & 5 Onsite testing for ABB UPS & STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | PUR | "Category: --- Identifier: --- Level 4 & 5 Onsite testing for ABB UPS & STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W
133441 | 5 | 1 | States | Oppidan Prineville | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 3 | 0 | 3 | 4500 | 13500 | 97754 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Mobilization | Mobilization - (3) Visit(s) | PUR | Mobilization - (3) Visit(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077401-11-1
133441 | 1 | 1 | States | Oppidan Prineville | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 16 | 0 | 16 | 10243 | 163888 | 97754 | USA | N45 | 1524 | ABB INC | 27511 | 1200A 24" Front Access Sidecar | SuperSwitch 4 - 1200A 24" Front Access Sidecar | PUR | SuperSwitch 4 - 1200A 24" Front Access Sidecar | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077401-11-1
133441 | 6 | 1 | States | Oppidan Prineville | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 8 | 0 | 8 | 4450 | 35600 | 97754 | USA | N45 | 1524 | ABB INC | 27511 | Services - Start-up Service | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | PUR | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077401-11-1
133441 | 3 | 1 | States | Oppidan Prineville | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 1 | 0 | 1 | 4255 | 4255 | 97754 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Integration Testing | Integration Testing - (1) Day(s) | PUR | Integration Testing - (1) Day(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077401-11-1
133441 | 9 | 1 | States | Oppidan Prineville | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 1 | 0 | 1 | 0 | 0 | 97754 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - Extended Warranty | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | PUR | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077401-11-1
133441 | 7 | 1 | States | Oppidan Prineville | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 16 | 0 | 16 | 95892 | 1534272 | 97754 | USA | N45 | 1524 | ABB INC | 27511 | SuperSwitch 4 (DSTS) | 1200A, 480V, DSTS (SS4) | PUR | 1200A, 480V, DSTS (SS4) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077401-11-1
133441 | 2 | 1 | States | Oppidan Prineville | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 16 | 0 | 16 | 390 | 6240 | 97754 | USA | N45 | 1524 | ABB INC | 27511 | 800A-1200A Vented Kickplates | SuperSwitch 4 - 800A-1200A Vented Kickplates | PUR | SuperSwitch 4 - 800A-1200A Vented Kickplates | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077401-11-1
133441 | 10 | 1 | States | Oppidan Prineville | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 1 | 0 | 1 | 86732 | 86732 | 97754 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - Extended Warranty | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | PUR | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077401-11-1
133441 | 4 | 1 | States | Oppidan Prineville | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 4255 | 17020 | 97754 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Level 4 | Level 4 Performancy Testing - (4) Days(s) | PUR | Level 4 Performancy Testing - (4) Days(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077401-11-1
133441 | 8 | 1 | States | Oppidan Prineville | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 96 | 0 | 96 | 57 | 5472 | 97754 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - STS | STS Pedestals | PUR | STS Pedestals | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077401-11-1
131309 | 1 | 1 | States | Champlin | Hayley Fabian | TRUE | 2026-02-17T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 15 | 0 | 15 | 5078.84 | 76182.6 | 55316 | USA | N60 | 1524 | ABB INC | 27511 | BTO ATS 400A-600A | ZGDK3XX12-CX2XT4XX Automatic Transfer Switch, ZTG T-Series, 400 A-600 A "ZTG DT 400A3PH No Neu N1 General Purpose Commercial and Industrial Automatic Transfer Switch 400 A, 3 Phase (3 Pole), Delayed Transition NEMA 1 Enclosure 4 NO (Normally Open) and 4 NC (Normally Closed) Auxiliary Contacts No Neutral No Meters GB2 - (6)#8-1/0 Ground Bar Modbus TCP communications Additional 4 I/O, programmable T1-Panel Voltage agnostic, Rated for 200 to 480V line to line voltage Standard Application-Sources on Bottom UL 1008 listed up To 480VAC at 50/60Hz Seismic certified To IEEE-693-2005 at HIGH level With 2.5 amplification factor Seismic certified To IBC-2015 at Ip=1.5 For z/h less than Or equal To 1 Microprocessor activated Momentary test switch Programmable exerciser daily, 7-14-28-365 days user- selectable, with or without load Event log of last 250 events Adjustable over/under frequency sensor-Source 2-and Source 1 Frequency Indication - on the controller LED Source -2 - Position indication LED Source -1 - Position indication LED Source -2 - Source availability indication LED Source -1 - Source availability indication" "Engine start timer -adjustable up to 60sec Phase rotation sensing of Source 1 and Source 2 Under voltage sensing 3-phase Source 2 In Phase Monitor between Source 1 and Source 2 to allow transfer-with enable/disable Over voltage sensing-3 phase Source 2 Microprocessor activated Commit/no commit on transferring to Source 2-with enable/disable Time Delay from Neutral Position to Source 1 on Retransfer Time Delay from Neutral Position to Source 2 on Retransfer. Adjustable time delay on transfer to Source 1 Engine stop/cool adjustable cool down timer Voltage imbalance between phases-applies to 3-phase only Adjustable time delay on transfer to Source 2 Bypass transfer timer function-soft switch in controller Programmable Input Modules: (Must be configured by user upon installation) E-Stop Remote Control to S1 (R15 Load Shed) Remote Control to S2 Remote Control to OFF (R15D Load Shed) Inhibit Transfer Manual-Auto Mode Programmable Output Modules: (Must be configured by user upon installation) Alarm / Product Availability Load Connected to S1 Load Disconnected Load Connected to S2 Elevator Pre-transfer Signal (T3/W3)" | PUR | ZGDK3XX12-CX2XT4XX Automatic Transfer Switch, ZTG T-Series, 400 A-600 A "ZTG DT 400A3PH No Neu N1 General Purpose Commercial and Industrial Automatic Transfer Switch 400 A, 3 Phase (3 Pole), Delayed Transition NEMA 1 Enclosure 4 NO (Normally Open) and 4 NC (Normally Closed) Auxiliary Contacts No Neutral No Meters GB2 - (6)#8-1/0 Ground Bar Modbus TCP communications Additional 4 I/O, programmable T1-Panel Voltage agnostic, Rated for 200 to 480V line to line voltage Standard Application-Sources on Bottom UL 1008 listed up To 480VAC at 50/60Hz Seismic certified To IEEE-693-2005 at HIGH level With 2.5 amplification factor Seismic certified To IBC-2015 at Ip=1.5 For z/h less than Or equal To 1 Microprocessor activated Momentary test switch Programmable exerciser daily, 7-14-28-365 days user- selectable, with or without load Event log of last 250 events Adjustable over/under frequency sensor-Source 2-and Source 1 Frequency Indication - on the controller LED Source -2 - Position indication LED Source -1 - Position indication LED Source -2 - Source availability indication LED Source -1 - Source availability indication" "Engine start timer -adjustable up to 60sec Phase rotation sensing of Source 1 and Source 2 Under voltage sensing 3-phase Source 2 In Phase Monitor between Source 1 and Source 2 to allow transfer-with enable/disable Over voltage sensing-3 phase Source 2 Microprocessor activated Commit/no commit on transferring to Source 2-with enable/disable Time Delay from Neutral Position to Source 1 on Retransfer Time Delay from Neutral Position to Source 2 on Retransfer. Adjustable time delay on transfer to Source 1 Engine stop/cool adjustable cool down timer Voltage imbalance between phases-applies to 3-phase only Adjustable time delay on transfer to Source 2 Bypass transfer timer function-soft switch in controller Programmable Input Modules: (Must be configured by user upon installation) E-Stop Remote Control to S1 (R15 Load Shed) Remote Control to S2 Remote Control to OFF (R15D Load Shed) Inhibit Transfer Manual-Auto Mode Programmable Output Modules: (Must be configured by user upon installation) Alarm / Product Availability Load Connected to S1 Load Disconnected Load Connected to S2 Elevator Pre-transfer Signal (T3/W3)" | EA | EA |  | TRUE |  | P | B/W | 100
134062 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-06-12T00:00:00 | 2027-02-08T00:00:00 | 2027-02-08T00:00:00 | 66 | 0 | 66 | 177.65 | 11724.9 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 991AJ05G01 | DOOR MOUNTED Current Test Switches, ABB | PUR | DOOR MOUNTED Current Test Switches, ABB | EA | EA |  | TRUE |  | P | B/W | DAYTON
132824 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-28T00:00:00 | 2026-09-23T00:00:00 | 2026-09-23T00:00:00 | 1 | 0 | 1 | 5206.44 | 5206.44 | 55369 | USA | N45 | 1524 | ABB INC | 27511 | CPTB951513800D151 | Control Power Transformer: 95 kV BIL, 15 kVA, 15 kV NSV, Primary voltage: 13800, Secondary voltage, 120/240 | PUR | Control Power Transformer: 95 kV BIL, 15 kVA, 15 kV NSV, Primary voltage: 13800, Secondary voltage, 120/240 | EA | EA |  | TRUE |  | P | B/W | DAYTON
133448 | 7 | 1 | States | Caddell Construction | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 95892 | 1534272 | 89506 | USA | N45 | 1524 | ABB INC | 27511 | SuperSwitch 4 (DSTS) | 1200A, 480V, DSTS (SS4) | PUR | 1200A, 480V, DSTS (SS4) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077404-11-1
133448 | 5 | 1 | States | Caddell Construction | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 3 | 0 | 3 | 4500 | 13500 | 89506 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Mobilization | Mobilization - (3) Visit(s) | PUR | Mobilization - (3) Visit(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077404-11-1
133448 | 9 | 1 | States | Caddell Construction | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 86732 | 86732 | 89506 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - Extended Warranty | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | PUR | 2 Year Extended Warranty w/1 PM QTY (16) 1200A STS Units | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077404-11-1
133448 | 2 | 1 | States | Caddell Construction | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 390 | 6240 | 89506 | USA | N45 | 1524 | ABB INC | 27511 | 800A-1200A Vented Kickplates | SuperSwitch 4 - 800A-1200A Vented Kickplates | PUR | SuperSwitch 4 - 800A-1200A Vented Kickplates | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077404-11-1
133448 | 8 | 1 | States | Caddell Construction | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 96 | 0 | 96 | 57 | 5472 | 89506 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - STS | STS Pedestals | PUR | STS Pedestals | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077404-11-1
133448 | 4 | 1 | States | Caddell Construction | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 4255 | 17020 | 89506 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Level 4 | Level 4 Performancy Testing - (4) Days(s) | PUR | Level 4 Performancy Testing - (4) Days(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077404-11-1
133448 | 1 | 1 | States | Caddell Construction | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 10243 | 163888 | 89506 | USA | N45 | 1524 | ABB INC | 27511 | 1200A 24" Front Access Sidecar | SuperSwitch 4 - 1200A 24" Front Access Sidecar | PUR | SuperSwitch 4 - 1200A 24" Front Access Sidecar | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077404-11-1
133448 | 3 | 1 | States | Caddell Construction | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 4255 | 4255 | 89506 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Integration Testing | Integration Testing - (1) Day(s) | PUR | Integration Testing - (1) Day(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077404-11-1
133448 | 6 | 1 | States | Caddell Construction | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 4450 | 35600 | 89506 | USA | N45 | 1524 | ABB INC | 27511 | Services - Start-up Service | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | PUR | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077404-11-1
133981 | 1 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-06-10T00:00:00 | 2026-09-25T00:00:00 | 2026-09-25T00:00:00 | 32 | 0 | 32 | 5296.1 | 312469.9 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CB11L1211BY00U | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: L - Lower, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: L - Lower, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | dayton
133981 | 2 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-06-10T00:00:00 | 2026-09-25T00:00:00 | 2026-09-25T00:00:00 | 16 | 0 | 16 | 5296.1 | 169475.2 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CB11U1211BY00U | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: U - Upper, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: U - Upper, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
133981 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-06-10T00:00:00 | 2026-09-25T00:00:00 | 2026-09-25T00:00:00 | 27 | 0 | 27 | 5296.1 | 312469.9 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CB11L1211BY00U | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: L - Lower, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: L - Lower, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | dayton
133981 | 2 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-06-10T00:00:00 | 2026-09-25T00:00:00 | 2026-09-25T00:00:00 | 16 | 0 | 16 | 5296.1 | 169475.2 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CB11U1211BY00U | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: U - Upper, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: U - Upper, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
135240 | 2 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-08-05T00:00:00 | 2026-12-31T00:00:00 | 2026-12-31T00:00:00 | 3 | 0 | 3 | 310.96 | 932.88 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 7525A33G10 | Current Transformer: Model SCH-3, 600:5 ratio, 3" Window | PUR | Current Transformer: Model SCH-3, 600:5 ratio, 3" Window | EA | EA |  | TRUE |  | P | B/W | DAYTON
135240 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-08-05T00:00:00 | 2026-11-05T00:00:00 | 2026-11-05T00:00:00 | 1 | 0 | 1 | 255 | 255 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | C498A010G01 | Test Switch: 10 pole, 4-potential (red handle), 6-current (black handle), FT1 (T T T T C-C C-C C-C) Clear Cover, Screw Terminals | PUR | Test Switch: 10 pole, 4-potential (red handle), 6-current (black handle), FT1 (T T T T C-C C-C C-C) Clear Cover, Screw Terminals | EA | EA |  | TRUE |  | P | B/W | Dayton
131640 | 4 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-05T00:00:00 | 2026-09-22T00:00:00 | 2026-09-22T00:00:00 | 72 | 71 | 1 | 2104.16 | 151499.52 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | 9629A02G10 | VIZ-11, INDOOR application, 110 kV BIL, Nominal system voltage: 15 kV, Connection type: LINE-GROUND, Primary voltage: 14400/14400GY Volts, Secondary voltage: 120 & 120, Metering accuracy: 0.3Y & 0.3Y, RVF: 1.1, Thermal rating: 1500, Frequency: 60 | PUR | VIZ-11, INDOOR application, 110 kV BIL, Nominal system voltage: 15 kV, Connection type: LINE-GROUND, Primary voltage: 14400/14400GY Volts, Secondary voltage: 120 & 120, Metering accuracy: 0.3Y & 0.3Y, RVF: 1.1, Thermal rating: 1500, Frequency: 60 | EA | EA |  | TRUE |  | P | B/W | DAYTON
132352 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-09T00:00:00 | 2026-12-23T00:00:00 | 2026-12-23T00:00:00 | 1 | 0 | 1 | 22200 | 22200 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | Level 4 & 5 Onsite testing for ABB UPS & STS | Category: --- Identifier: --- Level 4 & 5 Onsite testing for ABB UPS & STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | PUR | Category: --- Identifier: --- Level 4 & 5 Onsite testing for ABB UPS & STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | TRUE |  | P | B/W
135593 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-08-20T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 193 | 0 | 193 | 101 | 19493 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 2RKA024750A0001 | Adapter plate for KECA 80 current sensor | PUR | Adapter plate for KECA 80 current sensor | EA | EA |  | TRUE |  | P | B/W | DAYTON
135852 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-09-01T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 77 | 0 | 77 | 101 | 7777 | 55369 | USA | N45 | 1524 | ABB INC | 27511 | 2RKA024750A0001 | Adapter plate for KECA 80 current sensor | PUR | Adapter plate for KECA 80 current sensor | EA | EA |  | TRUE |  | P | B/W | DAYTON
134317 | 2 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-06-26T00:00:00 | 2026-09-25T00:00:00 | 2026-09-25T00:00:00 | 4 | 0 | 4 | 896 | 3584 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 966037K01 | MAIN BUS SUPPORT ASSY | PUR | MAIN BUS SUPPORT ASSY | EA | EA |  | TRUE |  | P | B/W | DAYTON
132287 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-07T00:00:00 | 2026-12-22T00:00:00 | 2026-12-22T00:00:00 | 1 | 0 | 1 | 22200 | 22200 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | Level 4 & 5 Onsite testing for ABB UPS & STS | Category: --- Identifier: --- Level 4 & 5 Onsite testing for ABB UPS & STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | PUR | "Category: --- Identifier: --- Level 4 & 5 Onsite testing for ABB UPS & STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W
132160 | 9 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-31T00:00:00 | 2026-09-30T00:00:00 | 2026-09-03T00:00:00 | 9 | 0 | 9 | 20822.82 | 187405.38 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | MA4Q11A000000U00 | 27KV DRAWOUT BREAKER, 1200A, 25KA, 120VAC CONTROL | PUR | 27KV DRAWOUT BREAKER, 1200A, 25KA, 120VAC CONTROL | EA | EA |  | TRUE |  | P | B/W | DAYTON
132160 | 11 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-31T00:00:00 | 2026-10-05T00:00:00 | 2026-07-23T00:00:00 | 9 | 0 | 9 | 8619.35 | 77574.15 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | 1YEC241980Z001 | Breaker compartment, 27kV@25kA, Epoxy 27kV 1200A. Upper/Lower position | PUR | Breaker compartment, 27kV@25kA, Epoxy 27kV 1200A. Upper/Lower position | EA | EA |  | TRUE |  | P | B/W | DAYTON | 2026-07-23T00:00:00
132160 | 13 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-31T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 1 | 0 | 1 | 11800 | 11800 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | 1YEC249999Z101 | DRAWOUT PT CRADLE | PUR | DRAWOUT PT CRADLE | EA | EA |  | TRUE |  | P | B/W | DAYTON
132160 | 7 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-31T00:00:00 | 2027-01-19T00:00:00 | 2027-01-19T00:00:00 | 3 | 0 | 3 | 3719.4 | 11158.2 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | 923A116G12 | VIZ-12G, INDOOR application, 125 kV BIL, Nominal system voltage: 27 kV, Connection type: LINE-LINE, Primary voltage: 24000/24000GY Volts, Secondary voltage: 120, Metering accuracy: 0.3Z, RVF: 1.1, Thermal rating: 1500, Frequency: 60, Ratio: 200:1 | PUR | VIZ-12G, INDOOR application, 125 kV BIL, Nominal system voltage: 27 kV, Connection type: LINE-LINE, Primary voltage: 24000/24000GY Volts, Secondary voltage: 120, Metering accuracy: 0.3Z, RVF: 1.1, Thermal rating: 1500, Frequency: 60, Ratio: 200:1 | EA | EA |  | TRUE |  | P | B/W | DAYTON
132584 | 12 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 14250 | 57000 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | FSUMEG1600P1 | Level-3 Startup of MegaFlex UPS | PUR | Level-3 Startup of MegaFlex UPS | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 2 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 32 | 0 | 32 | 31695.62 | 1014259.84 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 4NWP104024R36U2, 8 LiBC/UPS | Samsung 136S Lithium Battery Cabinets/UPS: - High cycle / High Power Density - UL9540/UL9540A Listed - Top Cable Entry - DC Breaker in each battery cabinet - DIM/BC: 25.5 in W x 21 in D x 87 in H; - Approx Weight/BC: 1125 lbs - Battery runtime: 7 minn BOL / 5 min EOL for 1579 kWb battery loads | PUR | Samsung 136S Lithium Battery Cabinets/UPS: - High cycle / High Power Density - UL9540/UL9540A Listed - Top Cable Entry - DC Breaker in each battery cabinet - DIM/BC: 25.5 in W x 21 in D x 87 in H; - Approx Weight/BC: 1125 lbs - Battery runtime: 7 minn BOL / 5 min EOL for 1579 kWb battery loads | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 17 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 2 | 0 | 2 | 4750 | 9500 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE | Level-3 Startup: Additional startup time - interfacing with and checking of Maintenance Bypass Switchboards (not actual SU of MBC or MBS) | PUR | Level-3 Startup: Additional startup time - interfacing with and checking of Maintenance Bypass Switchboards (not actual SU of MBC or MBS) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 1 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 1504.2 | 6016.8 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 4NWA7000321568A | MegaFlex Seismic Bracket | PUR | MegaFlex Seismic Bracket | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 10 | 2 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 4000 | 32000 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | FREIGHT_RIC | Freight: Incoterm FCA Factory - Freight allowed | PUR | Freight: Incoterm FCA Factory - Freight allowed | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 20 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | S-OST | Par 3.4.K - Onsite Training after startup/commissioning completion, contiguous US only (1 day / site + daily rate applied if exceeds) | PUR | Par 3.4.K - Onsite Training after startup/commissioning completion, contiguous US only (1 day / site + daily rate applied if exceeds) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 6 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 28 | 0 | 28 | 1653.75 | 46305 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 4NWR002204 | IntraPack Part No.: F012384-A02, Secondary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black | PUR | IntraPack Part No.: F012384-A02, Secondary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 18 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 16 | 0 | 16 | 4750 | 76000 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE Spec | Spec 263353.1, Par 3.2.B - Battery installation by UPS Manufacturer | PUR | Spec 263353.1, Par 3.2.B - Battery installation by UPS Manufacturer | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 19 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 4750 | 19000 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | S-IST | (1 day/UPS is recommended) Spec 263353, Par 3.6A Level-5 Integration System Testing (IST) (1 day included + daily rate applied if exceeds) | PUR | (1 day/UPS is recommended) Spec 263353, Par 3.6A Level-5 Integration System Testing (IST) (1 day included + daily rate applied if exceeds) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 7 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 3252.38 | 13009.52 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 4NWR002253 | IntraPack Part No.: F012382-A02, Standard Primary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black - Data logger provided by ABB | PUR | IntraPack Part No.: F012382-A02, Standard Primary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black - Data logger provided by ABB | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 5 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 1864.75 | 7459 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 4NWPN7574R0001 | Data Logger (w/o top hat), provided by ABB to be installed by IntraPack in the Primary Top hat | PUR | Data Logger (w/o top hat), provided by ABB to be installed by IntraPack in the Primary Top hat | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 23 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 5682.78 | 22731.12 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | UPS-FOBDEST_ | FCA Destination Charges Included | PUR | FCA Destination Charges Included | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 3 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 317079.24 | 1268316.96 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 4NWP106511R0002 | MegaFlex 1.5MW UPS 480V 60Hz: Static Bypass - 100% rated continuous duty; Cabinet color: RAL 9005 (black); Single or dual AC feed; Short circuit withstand rating: 100kAIC; Input Voltage: 480V 3-Phase + Gnd , +/- 15% voltage tolerance, Frequency: 60Hz +/- 10%, PF = 0.99; Output: 480V, 3W + Gnd, Frequency: 60Hz & PF = 1.0; Efficiency: Up to 97% Double Conversion (VFI) & Up to 99% eBoost mode (VFD); Compatible Battery Technologies: LiB, NiZn, VRLA | PUR | MegaFlex 1.5MW UPS 480V 60Hz: Static Bypass - 100% rated continuous duty; Cabinet color: RAL 9005 (black); Single or dual AC feed; Short circuit withstand rating: 100kAIC; Input Voltage: 480V 3-Phase + Gnd , +/- 15% voltage tolerance, Frequency: 60Hz +/- 10%, PF = 0.99; Output: 480V, 3W + Gnd, Frequency: 60Hz & PF = 1.0; Efficiency: Up to 97% Double Conversion (VFI) & Up to 99% eBoost mode (VFD); Compatible Battery Technologies: LiB, NiZn, VRLA | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 26 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 0 | 0 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 4NWP107801R0001 | ANC-L Network Communication Card | PUR | ANC-L Network Communication Card | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 8 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 13880.48 | 55521.92 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 79-5000-00000047 | 4000A DC Junction Cabinet: - NEMA-1 enclosure - Dim: 30"W x 24"D x 87"H - Front access; - Installed end cap of battery lineup closer to UPS I/O section - Accommodates up to 10 DC battery cabinet landings - Installed by contractor - see ABB installation drawing; | PUR | 4000A DC Junction Cabinet: - NEMA-1 enclosure - Dim: 30"W x 24"D x 87"H - Front access; - Installed end cap of battery lineup closer to UPS I/O section - Accommodates up to 10 DC battery cabinet landings - Installed by contractor - see ABB installation drawing; | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 15 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 8 | 0 | 8 | 4750 | 38000 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | S-CM1_UPS 3.5.B | Spec 263353, Par 3.5.B Level-4 Performance Testing per system Par 3.5.B: 2 days onsite (Deviate from 10 to 2 days per Customer Request) | PUR | Spec 263353, Par 3.5.B Level-4 Performance Testing per system Par 3.5.B: 2 days onsite (Deviate from 10 to 2 days per Customer Request) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 16 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 8 | 0 | 8 | 4750 | 38000 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | S-CM1_UPS 3.5.D | (Customer to decide) Spec 263353, Par 3.5.D Level-4 Performance Testing per system Par 3.5.D: Exploratory period - 1st 2 days onsite Note: Customer to decide if this step is necessary | PUR | (Customer to decide) Spec 263353, Par 3.5.D Level-4 Performance Testing per system Par 3.5.D: Exploratory period - 1st 2 days onsite Note: Customer to decide if this step is necessary | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 9 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 8 | 0 | 8 | 1750.5 | 14004 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 7GSP017351R0001 | UPS OPT IM0171E CUSTOMER INTERFAIEC_1605 | PUR | CIC Communication Card | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 24 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 34500 | 138000 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | WARMEG-2.2 | Provide 2 year extended warranty with annual PM of UPS & batteries |  | Provide 2 year extended warranty with annual PM of UPS & batteries | EA | EA |  | TRUE |  | P | B/W |  |  | 077373-1-1
132584 | 13 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | MOBILIZATION_UPS | Mobilization for UPS Pkg (assume startup at same time for both UPS's) | PUR | Mobilization for UPS Pkg (assume startup at same time for both UPS's) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 11 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 9500 | 38000 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | FSULITHI136X8P1 | Level-3 Startup of Lithium-Ion Batteries Note: Installation & connecting of batteries in the cabinets are by others (per adder above) | PUR | Level-3 Startup of Lithium-Ion Batteries Note: Installation & connecting of batteries in the cabinets are by others (per adder above) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 22 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 6441.69 | 25766.76 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | UPS-FOBDEST | FCA Destination Charges Included | PUR | FCA Destination Charges Included | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 10 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 4 | 0 | 4 | 4000 | 32000 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | FREIGHT_RIC | Freight: Incoterm FCA Factory - Freight allowed | PUR | Freight: Incoterm FCA Factory - Freight allowed | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132584 | 14 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-17T00:00:00 | 2027-05-17T00:00:00 | 2027-05-17T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | MOBILIZATION_UPS PKG | Mobilization for UPS Pkg (for L4/L5/L6T Tasks) | PUR | Mobilization for UPS Pkg (for L4/L5/L6T Tasks) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077373-1-1
132011 | 3 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-24T00:00:00 | 2026-09-25T00:00:00 | 2026-09-25T00:00:00 | 20 | 0 | 20 | 2877 | 57540 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | 931868T01 | Breaker Lift Truck Assembly - manually operated | PUR | Breaker Lift Truck Assembly - manually operated | EA | EA |  | TRUE |  | P | B/W | DAYTON
132011 | 2 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-24T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 121 | 0 | 121 | 216.75 | 26226.75 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | 498A010G01 | Test Switch: 10 pole, 4-potential (red handle), 6-current (black handle), FT1 (T T T T C-C C-C C-C) Screw Terminals | PUR | Test Switch: 10 pole, 4-potential (red handle), 6-current (black handle), FT1 (T T T T C-C C-C C-C) Screw Terminals | EA | EA |  | TRUE |  | P | B/W | DAYTON
133014 | 8 | 4 | States | Dayton | Hayley Fabian | TRUE | 2026-05-06T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 16 | 0 | 16 | 23024.2 | 1473548.8 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AA4X17777X000000 | ADVAC38; 4 - Model 4; A - Drawout; X1 - 40.5kV, 1200A, 25kA, 3 Cycle; CAP Switching: None; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: 7 - 125VDC; Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | PUR | ADVAC38; 4 - Model 4; A - Drawout; X1 - 40.5kV, 1200A, 25kA, 3 Cycle; CAP Switching: None; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: 7 - 125VDC; Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
133014 | 9 | 4 | States | Dayton | Hayley Fabian | TRUE | 2026-05-06T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 16 | 0 | 16 | 19093.11 | 1221959.04 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CBRL12122BY000 | Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 2 - 25 kA, CTs Kits: 1 - 6 CTs per compartment, TOC Harness: 2 - 16 Contacts, Door Type: B - LH Door, Door Stop: Y - Yes, SmartRack: 0 - None | PUR | Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 2 - 25 kA, CTs Kits: 1 - 6 CTs per compartment, TOC Harness: 2 - 16 Contacts, Door Type: B - LH Door, Door Stop: Y - Yes, SmartRack: 0 - None | EA | EA |  | TRUE |  | P | B/W | DAYTON
133014 | 8 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-06T00:00:00 | 2026-09-28T00:00:00 | 2026-09-04T00:00:00 | 10 | 0 | 10 | 23024.2 | 1473548.8 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AA4X17777X000000 | ADVAC38; 4 - Model 4; A - Drawout; X1 - 40.5kV, 1200A, 25kA, 3 Cycle; CAP Switching: None; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: 7 - 125VDC; Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | PUR | ADVAC38; 4 - Model 4; A - Drawout; X1 - 40.5kV, 1200A, 25kA, 3 Cycle; CAP Switching: None; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: 7 - 125VDC; Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
133014 | 9 | 3 | States | Dayton | Hayley Fabian | TRUE | 2026-05-06T00:00:00 | 2026-10-05T00:00:00 | 2026-10-05T00:00:00 | 24 | 0 | 24 | 19093.11 | 1221959.04 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CBRL12122BY000 | Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 2 - 25 kA, CTs Kits: 1 - 6 CTs per compartment, TOC Harness: 2 - 16 Contacts, Door Type: B - LH Door, Door Stop: Y - Yes, SmartRack: 0 - None | PUR | Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 2 - 25 kA, CTs Kits: 1 - 6 CTs per compartment, TOC Harness: 2 - 16 Contacts, Door Type: B - LH Door, Door Stop: Y - Yes, SmartRack: 0 - None | EA | EA |  | TRUE |  | P | B/W | DAYTON
133014 | 10 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-06T00:00:00 | 2026-10-22T00:00:00 | 2026-10-22T00:00:00 | 14 | 0 | 14 | 304 | 14592 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 14039G00 | ADVAC Breaker Accessory Kit - racking crank, manual charging handle, & lift yoke | PUR | ADVAC Breaker Accessory Kit - racking crank, manual charging handle, & lift yoke | EA | EA |  | TRUE |  | P | B/W | Dayton
133014 | 9 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-06T00:00:00 | 2026-09-28T00:00:00 | 2026-09-04T00:00:00 | 10 | 0 | 10 | 19093.11 | 1221959.04 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CBRL12122BY000 | Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 2 - 25 kA, CTs Kits: 1 - 6 CTs per compartment, TOC Harness: 2 - 16 Contacts, Door Type: B - LH Door, Door Stop: Y - Yes, SmartRack: 0 - None | PUR | Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 2 - 25 kA, CTs Kits: 1 - 6 CTs per compartment, TOC Harness: 2 - 16 Contacts, Door Type: B - LH Door, Door Stop: Y - Yes, SmartRack: 0 - None | EA | EA |  | TRUE |  | P | B/W | DAYTON
133014 | 8 | 3 | States | Dayton | Hayley Fabian | TRUE | 2026-05-06T00:00:00 | 2026-10-05T00:00:00 | 2026-10-05T00:00:00 | 24 | 0 | 24 | 23024.2 | 1473548.8 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AA4X17777X000000 | ADVAC38; 4 - Model 4; A - Drawout; X1 - 40.5kV, 1200A, 25kA, 3 Cycle; CAP Switching: None; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: 7 - 125VDC; Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | PUR | ADVAC38; 4 - Model 4; A - Drawout; X1 - 40.5kV, 1200A, 25kA, 3 Cycle; CAP Switching: None; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: 7 - 125VDC; Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
133841 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-06-03T00:00:00 | 2026-11-05T00:00:00 | 2026-11-05T00:00:00 | 12 | 0 | 12 | 979.86 | 11758.32 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 923A330G87-M | SAB-2, INDOOR application, 10 kV BIL, Nominal system voltage: 0.6 kV, Primary current: 300 Amps, Secondary current: 5SR, Rating factor: 2.0, Metering Accuracy: NONE, Relay Accuracy: C50, Frequency: 60Hz, Window size (inches): 6.5 WHEN ORDERING REFERENCE QUOTE# 99Q2025100767283 SAVED IN THE VENDOR QUOTES FOLDER | PUR | SAB-2, INDOOR application, 10 kV BIL, Nominal system voltage: 0.6 kV, Primary current: 300 Amps, Secondary current: 5SR, Rating factor: 2.0, Metering Accuracy: NONE, Relay Accuracy: C50, Frequency: 60Hz, Window size (inches): 6.5 WHEN ORDERING REFERENCE QUOTE# 99Q2025100767283 SAVED IN THE VENDOR QUOTES FOLDER | EA | EA |  | TRUE |  | P | B/W | DAYTON
134674 | 1 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 40 | 0 | 40 | 476.85 | 40055.4 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | FT4D14T12BN4780-04 | FT4D14T12BN4780-04 FT14D (FT4D14T12BN4780-04 - FT-14D Digital Test Switch; 12 potential poles, w/ RJ45 connectors; Black Cover, w/ labels Ig x1, and Ig x2 on current terminals 13 & 14 (IEC 61869-10 and IEC 60044-8 sensors, relays compatible) | PUR | FT4D14T12BN4780-04 FT14D (FT4D14T12BN4780-04 - FT-14D Digital Test Switch; 12 potential poles, w/ RJ45 connectors; Black Cover, w/ labels Ig x1, and Ig x2 on current terminals 13 & 14 (IEC 61869-10 and IEC 60044-8 sensors, relays compatible) | EA | EA |  | TRUE |  | P | B/W | DAYTON
134674 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 44 | 0 | 44 | 476.85 | 40055.4 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | FT4D14T12BN4780-04 | FT4D14T12BN4780-04 FT14D (FT4D14T12BN4780-04 - FT-14D Digital Test Switch; 12 potential poles, w/ RJ45 connectors; Black Cover, w/ labels Ig x1, and Ig x2 on current terminals 13 & 14 (IEC 61869-10 and IEC 60044-8 sensors, relays compatible) | PUR | FT4D14T12BN4780-04 FT14D (FT4D14T12BN4780-04 - FT-14D Digital Test Switch; 12 potential poles, w/ RJ45 connectors; Black Cover, w/ labels Ig x1, and Ig x2 on current terminals 13 & 14 (IEC 61869-10 and IEC 60044-8 sensors, relays compatible) | EA | EA |  | TRUE |  | P | B/W | DAYTON
135985 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-09-09T00:00:00 | 2026-12-17T00:00:00 | 2026-12-17T00:00:00 | 49 | 0 | 49 | 177.65 | 8704.85 | 55369 | USA | N45 | 1524 | ABB INC | 27511 | 991AJ05G01 | DOOR MOUNTED Current Test Switches, ABB | PUR | DOOR MOUNTED Current Test Switches, ABB | EA | EA |  | TRUE |  | P | B/W | DAYTON
135587 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-08-19T00:00:00 | 2026-10-22T00:00:00 | 2026-10-22T00:00:00 | 1 | 0 | 1 | 969.88 | 969.88 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 186-023-422 | HE Shaft Drive with Mech Interlock and Kirk Key, Right Side, Offset for all Rating Switches | PUR | HE Shaft Drive with Mech Interlock and Kirk Key, Right Side, Offset for all Rating Switches | EA | EA |  | TRUE |  | P | B/W | DAYTON
132290 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-07T00:00:00 | 2026-12-22T00:00:00 |  | 1 | 0 | 1 | 0 | 0 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | BTO 250A STS | Category: --- LV - Other --- Identifier: --- BTO 250A STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | PUR | "Category: --- LV - Other --- Identifier: --- BTO 250A STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | FALSE |  | P | B/W | Dayton
132136 | 8 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-30T00:00:00 | 2026-09-14T00:00:00 | 2026-06-30T00:00:00 | 61 | 0 | 61 | 30183.51 | 2082662.19 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AB4Z1777XX000000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | MVMS | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | Dayton
132136 | 10 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-30T00:00:00 | 2026-09-14T00:00:00 | 2026-07-10T00:00:00 | 80 | 24 | 56 | 19818.59 | 1585487.2 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CBRL14221AY000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Product Type: CB - Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 4 - 40 kA, CTs Kits: 2 - 12 CTs per compartment, TOC Harness: 1 - 8 Contacts, Door Type: A - RH Door, Door Stop: Y - Yes, SmartRack: 0 - None | PUR | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Product Type: CB - Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 4 - 40 kA, CTs Kits: 2 - 12 CTs per compartment, TOC Harness: 1 - 8 Contacts, Door Type: A - RH Door, Door Stop: Y - Yes, SmartRack: 0 - None | EA | EA |  | TRUE |  | P | B/W | Dayton
132136 | 9 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-30T00:00:00 | 2026-09-14T00:00:00 | 2026-06-30T00:00:00 | 4 | 2 | 2 | 35333.2 | 141332.8 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AB4Z2777XX000000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z2 - 40.5kV, 2000A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | PUR | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z2 - 40.5kV, 2000A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
132414 | 2 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-10T00:00:00 | 2027-01-29T00:00:00 | 2027-01-29T00:00:00 | 12 | 0 | 12 | 390 | 4680 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 800A-1200A Vented Kickplates | SuperSwitch 4 - 800A-1200A Vented Kickplates | PUR | SuperSwitch 4 - 800A-1200A Vented Kickplates | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077374-2-1
132414 | 4 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-10T00:00:00 | 2027-04-30T00:00:00 | 2027-04-30T00:00:00 | 3 | 0 | 3 | 4500 | 13500 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Mobilization | Mobilization - (3) Visit(s) | PUR | Mobilization - (3) Visit(s) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077374-2-1
132414 | 8 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-10T00:00:00 | 2027-04-30T00:00:00 | 2027-04-30T00:00:00 | 1 | 0 | 1 | 4255 | 4255 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Integration Testing | Integration Testing - (1) Day(s) | PUR | Integration Testing - (1) Day(s) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077374-2-1
132414 | 7 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-10T00:00:00 | 2027-01-29T00:00:00 | 2027-01-29T00:00:00 | 72 | 0 | 72 | 57 | 4104 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - STS | STS Pedestals | PUR | STS Pedestals | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077374-2-1
132414 | 1 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-10T00:00:00 | 2027-01-29T00:00:00 | 2027-01-29T00:00:00 | 12 | 0 | 12 | 9500 | 114000 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | 1200A 24" Front Access Sidecar | SuperSwitch 4 - 1200A 24" Front Access Sidecar | PUR | SuperSwitch 4 - 1200A 24" Front Access Sidecar | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077374-2-1
132414 | 6 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-10T00:00:00 | 2027-01-29T00:00:00 | 2027-01-29T00:00:00 | 12 | 0 | 12 | 95892 | 1150704 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | SuperSwitch 4 (DSTS) | 1200A, 480V, DSTS (SS4) | PUR | 1200A, 480V, DSTS (SS4) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077374-2-1
132414 | 3 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-10T00:00:00 | 2027-04-30T00:00:00 | 2027-04-30T00:00:00 | 4 | 0 | 4 | 4255 | 17020 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Level 4 | Level 4 Performancy Testing - (4) Days(s) | PUR | Level 4 Performancy Testing - (4) Days(s) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077374-2-1
132414 | 5 | 1 | States | Oppidan | Hayley Fabian | TRUE | 2026-04-10T00:00:00 | 2027-04-30T00:00:00 | 2027-04-30T00:00:00 | 6 | 0 | 6 | 4450 | 26700 | 53916 | USA | N45 | 1524 | ABB INC | 27511 | Services - Start-up Service | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | PUR | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077374-2-1
132725 | 11 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-23T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 1 | 0 | 1 | 2405.4 | 2405.4 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CL3YBY0000000U | Product Type: C - LV Compartment, Compartment Height: 3 - 57 Inch, Bottom IT Pans: Y - Yes, Door Type: B - 57 Inch MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - LV Compartment, Compartment Height: 3 - 57 Inch, Bottom IT Pans: Y - Yes, Door Type: B - 57 Inch MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
132725 | 8 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-23T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 1 | 0 | 1 | 983.26 | 983.26 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 931773T06 | Main, Bus, Support, Assy, 1200A | PUR | Main, Bus, Support, Assy, 1200A | EA | EA |  | TRUE |  | P | B/W | Dayton
132725 | 12 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-23T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 2 | 0 | 2 | 3787.45 | 7574.9 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CP8A1W1NBY000U | Product Type: C - PT Compartment, Max Voltage: 15kV, Rated Voltage: 8 - 14.4 kV, Compartment Position: A - Position A, D, or E, Insulation Type: 1 - Polyester, Transformer Arrangement: W - (3) 1-Fuse Wye, Secondary Disconnect: 1 - With Secondary, PT and Fuse Equipment: N - Without PT and Fuse, Door Type: C - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - PT Compartment, Max Voltage: 15kV, Rated Voltage: 8 - 14.4 kV, Compartment Position: A - Position A, D, or E, Insulation Type: 1 - Polyester, Transformer Arrangement: W - (3) 1-Fuse Wye, Secondary Disconnect: 1 - With Secondary, PT and Fuse Equipment: N - Without PT and Fuse, Door Type: C - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
132725 | 14 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-23T00:00:00 | 2026-10-28T00:00:00 | 2026-10-28T00:00:00 | 9 | 0 | 9 | 1654.9 | 14894.1 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | REX615_10RD | ABB REX615A10GN+APP1+BIO5+CMP1+COM1+HMI1+PCL1+PSM4+SCT1+SIM5 PROTECTIVE RELAY | PUR | ABB REX615A10GN+APP1+BIO5+CMP1+COM1+HMI1+PCL1+PSM4+SCT1+SIM5 PROTECTIVE RELAY | EA | EA |  | TRUE |  | P | B/W | DAYTON
132725 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-23T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 1 | 0 | 1 | 567.04 | 567.04 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 14039G10 | AMVAC Breaker Accessory Kit - racking crank, manual opening handle, & lift yoke | PUR | AMVAC Breaker Accessory Kit - racking crank, manual opening handle, & lift yoke | EA | EA |  | TRUE |  | P | B/W | dayton
132725 | 13 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-23T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 2 | 0 | 2 | 10777.51 | 21555.02 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | MA4G116000000U0 | Circuit Breaker: AMVAC; 4 - Model 4; A - Drawout; G1 - 15kV, 1200A, 25kA, 3 Cycle; Control Scheme:1 - Dual secondary disconnect (Standard); Control Volt:6 - 48VDC; Application Card:0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: U - UL Recognized; Ground Cont:0 - Ground pad stainless steel | PUR | Circuit Breaker: AMVAC; 4 - Model 4; A - Drawout; G1 - 15kV, 1200A, 25kA, 3 Cycle; Control Scheme:1 - Dual secondary disconnect (Standard); Control Volt:6 - 48VDC; Application Card:0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: U - UL Recognized; Ground Cont:0 - Ground pad stainless steel | EA | EA |  | TRUE |  | P | B/W | DAYTON
132725 | 9 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-23T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 1 | 0 | 1 | 5296.1 | 5296.1 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CB11U1211BY00U | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: U - Upper, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: U - Upper, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
132725 | 10 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-23T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 1 | 0 | 1 | 1424.25 | 1424.25 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CL1YBY0000000U | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: B - 38 Inch MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: B - 38 Inch MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | dayton
133446 | 7 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 95892 | 1534272 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | SuperSwitch 4 (DSTS) | 1200A, 480V, DSTS (SS4) | PUR | 1200A, 480V, DSTS (SS4) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077403-11-1
133446 | 9 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 86732 | 86732 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - Extended Warranty | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | PUR | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077403-11-1
133446 | 1 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 10243 | 163888 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | 1200A 24" Front Access Sidecar | SuperSwitch 4 - 1200A 24" Front Access Sidecar | PUR | SuperSwitch 4 - 1200A 24" Front Access Sidecar | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077403-11-1
133446 | 6 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 4450 | 35600 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | Services - Start-up Service | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | PUR | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077403-11-1
133446 | 5 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 3 | 0 | 3 | 4500 | 13500 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Mobilization | Mobilization - (3) Visit(s) | PUR | Mobilization - (3) Visit(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077403-11-1
133446 | 3 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 4255 | 4255 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Integration Testing | Integration Testing - (1) Day(s) | PUR | Integration Testing - (1) Day(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077403-11-1
133446 | 4 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 4255 | 17020 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Level 4 | Level 4 Performancy Testing - (4) Days(s) | PUR | Level 4 Performancy Testing - (4) Days(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077403-11-1
133446 | 8 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 96 | 0 | 96 | 57 | 5472 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - STS | STS Pedestals | PUR | STS Pedestals | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077403-11-1
133446 | 2 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 390 | 6240 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | 800A-1200A Vented Kickplates | SuperSwitch 4 - 800A-1200A Vented Kickplates | PUR | SuperSwitch 4 - 800A-1200A Vented Kickplates | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077403-11-1
131089 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-02-04T00:00:00 | 2026-12-01T00:00:00 | 2026-12-01T00:00:00 | 15 | 0 | 15 | 5078.84 | 76182.6 | 55369 | USA | N45 | 1524 | ABB INC | 27511 | BTO ATS 400A-600A | ZGDK3XX12-CX2XT4XX Automatic Transfer Switch, ZTG T-Series, 400 A-600 A "ZTG DT 400A3PH No Neu N1 General Purpose Commercial and Industrial Automatic Transfer Switch 400 A, 3 Phase (3 Pole), Delayed Transition NEMA 1 Enclosure 4 NO (Normally Open) and 4 NC (Normally Closed) Auxiliary Contacts No Neutral No Meters GB2 - (6)#8-1/0 Ground Bar Modbus TCP communications Additional 4 I/O, programmable T1-Panel Voltage agnostic, Rated for 200 to 480V line to line voltage Standard Application-Sources on Bottom UL 1008 listed up To 480VAC at 50/60Hz Seismic certified To IEEE-693-2005 at HIGH level With 2.5 amplification factor Seismic certified To IBC-2015 at Ip=1.5 For z/h less than Or equal To 1 Microprocessor activated Momentary test switch Programmable exerciser daily, 7-14-28-365 days user- selectable, with or without load Event log of last 250 events Adjustable over/under frequency sensor-Source 2-and Source 1 Frequency Indication - on the controller LED Source -2 - Position indication LED Source -1 - Position indication LED Source -2 - Source availability indication LED Source -1 - Source availability indication" "Engine start timer -adjustable up to 60sec Phase rotation sensing of Source 1 and Source 2 Under voltage sensing 3-phase Source 2 In Phase Monitor between Source 1 and Source 2 to allow transfer-with enable/disable Over voltage sensing-3 phase Source 2 Microprocessor activated Commit/no commit on transferring to Source 2-with enable/disable Time Delay from Neutral Position to Source 1 on Retransfer Time Delay from Neutral Position to Source 2 on Retransfer. Adjustable time delay on transfer to Source 1 Engine stop/cool adjustable cool down timer Voltage imbalance between phases-applies to 3-phase only Adjustable time delay on transfer to Source 2 Bypass transfer timer function-soft switch in controller Programmable Input Modules: (Must be configured by user upon installation) E-Stop Remote Control to S1 (R15 Load Shed) Remote Control to S2 Remote Control to OFF (R15D Load Shed) Inhibit Transfer Manual-Auto Mode Programmable Output Modules: (Must be configured by user upon installation) Alarm / Product Availability Load Connected to S1 Load Disconnected Load Connected to S2 Elevator Pre-transfer Signal (T3/W3)" | PUR | "Category: --- LV - Other --- Identifier: --- BTO ATS 400A-600A ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | 100
135414 | 3 | 1 | States | Champlin | Hayley Fabian | TRUE | 2026-08-12T00:00:00 | 2026-09-21T00:00:00 | 2026-08-21T00:00:00 | 2 | 0 | 2 | 798 | 1596 | 55316-3157 | USA | N45 | 1524 | ABB INC | 27511 | 7GSP017351R0001 | UPS OPT IM0171E CUSTOMER INTERFAIEC_1605 | PUR | UPS OPT IM0171E CUSTOMER INTERFAIEC_1605 | EA | EA |  | TRUE |  | P | B/W | DAYTON
133449 | 8 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 96 | 0 | 96 | 57 | 5472 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - STS | STS Pedestals | PUR | STS Pedestals | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077405-12-1
133449 | 2 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 390 | 6240 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | 800A-1200A Vented Kickplates | SuperSwitch 4 - 800A-1200A Vented Kickplates | PUR | SuperSwitch 4 - 800A-1200A Vented Kickplates | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077405-12-1
133449 | 6 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 4450 | 35600 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | Services - Start-up Service | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | PUR | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077405-12-1
133449 | 9 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 86732 | 86732 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - Extended Warranty | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | PUR | 2 Year Extended Warranty w/1 PM QTY (16) 1200A STS Units | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077405-12-1
133449 | 4 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 4255 | 17020 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Level 4 | Level 4 Performancy Testing - (4) Days(s) | PUR | Level 4 Performancy Testing - (4) Days(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077405-12-1
133449 | 1 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 10243 | 163888 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | 1200A 24" Front Access Sidecar | SuperSwitch 4 - 1200A 24" Front Access Sidecar | PUR | SuperSwitch 4 - 1200A 24" Front Access Sidecar | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077405-12-1
133449 | 7 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 95892 | 1534272 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | SuperSwitch 4 (DSTS) | 1200A, 480V, DSTS (SS4) | PUR | 1200A, 480V, DSTS (SS4) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077405-12-1
133449 | 5 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 3 | 0 | 3 | 4500 | 13500 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Mobilization | Mobilization - (3) Visit(s) | PUR | Mobilization - (3) Visit(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077405-12-1
133449 | 3 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 4255 | 4255 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Integration Testing | Integration Testing - (1) Day(s) | PUR | Integration Testing - (1) Day(s) | EA | EA |  | FALSE |  | P | B/W | 100 |  | 077405-12-1
133065 | 4 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-09-28T00:00:00 | 2026-09-28T00:00:00 | 10 | 3 | 7 | 29821.31 | 3369808.03 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AB4Z1777XX000000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | MVMS | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | Dayton
133065 | 7 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-10-06T00:00:00 | 2026-09-21T00:00:00 | 51 | 0 | 51 | 8215.08 | 837938.16 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AA4C1777XX000U00 | ADVAC; 4 - Model 4; A - Drawout; C1 - 4.76kV, 1200A, 40kA, 5 Cycle; CAP Switching: Rated Cable Charging Cur. 25A; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Undervoltage: X - None (Dual Secondary Disconnect); Button Color: 0 - Standard (ANSI); Button Protection: 0 - None; UL: U - UL Recognized; Ground Contact: 0 - Ground pad stainless steel; Racking Mechanism: 0 - Manual Truck | PUR | ADVAC; 4 - Model 4; A - Drawout; C1 - 4.76kV, 1200A, 40kA, 5 Cycle; CAP Switching: Rated Cable Charging Cur. 25A; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Undervoltage: X - None (Dual Secondary Disconnect); Button Color: 0 - Standard (ANSI); Button Protection: 0 - None; UL: U - UL Recognized; Ground Contact: 0 - Ground pad stainless steel; Racking Mechanism: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
133065 | 10 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-11-10T00:00:00 | 2026-11-10T00:00:00 | 5 | 0 | 5 | 2877 | 14385 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 931868T01 | Breaker Lift Truck Assembly - manually operated | PUR | Breaker Lift Truck Assembly - manually operated | EA | EA |  | TRUE |  | P | B/W | DAYTON
133065 | 3 | 4 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 204 | 0 | 204 | 971.81 | 626817.45 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VL5400072V1202 | Current Sensors | PUR | Current Sensors | EA | EA |  | TRUE |  | P | B/W | DAYTON
133065 | 4 | 3 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 78 | 0 | 78 | 29821.31 | 3369808.03 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AB4Z1777XX000000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | MVMS | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | Dayton
133065 | 5 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 102 | 0 | 102 | 19580.76 | 1997237.52 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CBRL14221AY000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Product Type: CB - Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 4 - 40 kA, CTs Kits: 2 - 12 CTs per compartment, TOC Harness: 1 - 8 Contacts, Door Type: A - RH Door, Door Stop: Y - Yes, SmartRack: 0 - None | PUR | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Product Type: CB - Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 4 - 40 kA, CTs Kits: 2 - 12 CTs per compartment, TOC Harness: 1 - 8 Contacts, Door Type: A - RH Door, Door Stop: Y - Yes, SmartRack: 0 - None | EA | EA |  | TRUE |  | P | B/W | Dayton
133065 | 6 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-10-26T00:00:00 | 2026-10-19T00:00:00 | 14 | 0 | 14 | 1292.37 | 55571.91 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 925320T03 | CB Test Station, dual secondary, single trip (wall mounted) | PUR | CB Test Station, dual secondary, single trip (wall mounted) | EA | EA |  | TRUE |  | P | B/W | DAYTON
133065 | 7 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-09-28T00:00:00 | 2026-08-18T00:00:00 | 51 | 20 | 31 | 8215.08 | 837938.16 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AA4C1777XX000U00 | ADVAC; 4 - Model 4; A - Drawout; C1 - 4.76kV, 1200A, 40kA, 5 Cycle; CAP Switching: Rated Cable Charging Cur. 25A; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Undervoltage: X - None (Dual Secondary Disconnect); Button Color: 0 - Standard (ANSI); Button Protection: 0 - None; UL: U - UL Recognized; Ground Contact: 0 - Ground pad stainless steel; Racking Mechanism: 0 - Manual Truck | PUR | ADVAC; 4 - Model 4; A - Drawout; C1 - 4.76kV, 1200A, 40kA, 5 Cycle; CAP Switching: Rated Cable Charging Cur. 25A; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Undervoltage: X - None (Dual Secondary Disconnect); Button Color: 0 - Standard (ANSI); Button Protection: 0 - None; UL: U - UL Recognized; Ground Contact: 0 - Ground pad stainless steel; Racking Mechanism: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
133065 | 9 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-09-21T00:00:00 | 2026-09-21T00:00:00 | 51 | 0 | 51 | 30 | 3060 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 890577D00 | Breaker Interference Plate | PUR | Breaker Interference Plate | EA | EA |  | TRUE |  | P | B/W | dayton
133065 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-10-16T00:00:00 | 2026-10-16T00:00:00 | 14 | 0 | 14 | 9463.52 | 132489.28 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VCF549700R0580 | BREAKER LIFT TRUCK 38KV ADVAC | PUR | BREAKER LIFT TRUCK 38KV ADVAC | EA | EA |  | TRUE |  | P | B/W | DAYTON
133065 | 3 | 3 | States | Dayton | Hayley Fabian | TRUE | 2026-05-07T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 216 | 0 | 216 | 971.81 | 626817.45 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VL5400072V1202 | Current Sensors | PUR | Current Sensors | EA | EA |  | TRUE |  | P | B/W | DAYTON
133875 | 2 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-06-04T00:00:00 | 2026-10-21T00:00:00 | 2026-10-21T00:00:00 | 2 | 0 | 2 | 20822.82 | 41645.64 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | MA4Q117000000U00 | AMVAC; 4 - Model 4; A - Drawout; Q1 - 27kV, 1200A, 25kA, 2.5 Cycle; Control Scheme: 1 - Dual secondary disconnect (Standard); Control Voltage: 7 - 125VDC; Application Card: 0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: U - UL Recognized; Ground Contact: 0 - Ground pad stainless steel; Racking Mechanism: 0 - Manual Truck | PUR | AMVAC; 4 - Model 4; A - Drawout; Q1 - 27kV, 1200A, 25kA, 2.5 Cycle; Control Scheme: 1 - Dual secondary disconnect (Standard); Control Voltage: 7 - 125VDC; Application Card: 0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: U - UL Recognized; Ground Contact: 0 - Ground pad stainless steel; Racking Mechanism: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
133875 | 7 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-06-04T00:00:00 | 2026-10-21T00:00:00 | 2026-10-21T00:00:00 | 2 | 0 | 2 | 10777.51 | 21555.02 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | MA4G117000000U00 | AMVAC; 4 - Model 4; A - Drawout; G1 - 15kV, 1200A, 25kA, 3 Cycle; Control Scheme: 1 - Dual secondary disconnect (Standard); Control Voltage: 7 - 125VDC; Application Card: 0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: U - UL Recognized; Ground Contact: 0 - Ground pad stainless steel; Racking Mechanism: 0 - Manual Truck | PUR | AMVAC; 4 - Model 4; A - Drawout; G1 - 15kV, 1200A, 25kA, 3 Cycle; Control Scheme: 1 - Dual secondary disconnect (Standard); Control Voltage: 7 - 125VDC; Application Card: 0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: U - UL Recognized; Ground Contact: 0 - Ground pad stainless steel; Racking Mechanism: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
132048 | 4 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-03-25T00:00:00 | 2026-09-21T00:00:00 | 2026-04-13T00:00:00 | 32 | 0 | 32 | 17307.83 | 1730783 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | MF4Q12600000001F | AMVAC; 4 - Model 4; F - Fixed mounted breaker; Q1 - 27kV, 1200A, 25kA, 2.5 Cycle; Control Scheme: 2 - Fixed mounted dual secondary disconnect; Control Voltage: 6 - 48VDC; Application Card: 0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: 0 - None; Ground Contact: 1 - Standard fixed mount; Racking Mechanism: F - No Truck | PUR | AMVAC; 4 - Model 4; F - Fixed mounted breaker; Q1 - 27kV, 1200A, 25kA, 2.5 Cycle; Control Scheme: 2 - Fixed mounted dual secondary disconnect; Control Voltage: 6 - 48VDC; Application Card: 0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: 0 - None; Ground Contact: 1 - Standard fixed mount; Racking Mechanism: F - No Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
132048 | 4 | 3 | States | Dayton | Hayley Fabian | TRUE | 2026-03-25T00:00:00 | 2027-03-08T00:00:00 | 2026-06-05T00:00:00 | 34 | 0 | 34 | 17307.83 | 1730783 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | MF4Q12600000001F | AMVAC; 4 - Model 4; F - Fixed mounted breaker; Q1 - 27kV, 1200A, 25kA, 2.5 Cycle; Control Scheme: 2 - Fixed mounted dual secondary disconnect; Control Voltage: 6 - 48VDC; Application Card: 0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: 0 - None; Ground Contact: 1 - Standard fixed mount; Racking Mechanism: F - No Truck | PUR | AMVAC; 4 - Model 4; F - Fixed mounted breaker; Q1 - 27kV, 1200A, 25kA, 2.5 Cycle; Control Scheme: 2 - Fixed mounted dual secondary disconnect; Control Voltage: 6 - 48VDC; Application Card: 0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: 0 - None; Ground Contact: 1 - Standard fixed mount; Racking Mechanism: F - No Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
132048 | 1 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-03-25T00:00:00 | 2026-09-25T00:00:00 | 2026-07-20T00:00:00 | 6 | 0 | 6 | 8619.35 | 103432.2 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | 1YEC241980Z001 | Breaker compartment, 27kV@25kA, Epoxy 27kV 1200A. Upper/Lower position | PUR | Breaker compartment, 27kV@25kA, Epoxy 27kV 1200A. Upper/Lower position | EA | EA |  | TRUE |  | P | B/W | DAYTON | 2026-07-20T00:00:00
132048 | 4 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-25T00:00:00 | 2026-09-14T00:00:00 | 2026-06-05T00:00:00 | 34 | 24 | 10 | 17307.83 | 1730783 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | MF4Q12600000001F | AMVAC; 4 - Model 4; F - Fixed mounted breaker; Q1 - 27kV, 1200A, 25kA, 2.5 Cycle; Control Scheme: 2 - Fixed mounted dual secondary disconnect; Control Voltage: 6 - 48VDC; Application Card: 0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: 0 - None; Ground Contact: 1 - Standard fixed mount; Racking Mechanism: F - No Truck | PUR | AMVAC; 4 - Model 4; F - Fixed mounted breaker; Q1 - 27kV, 1200A, 25kA, 2.5 Cycle; Control Scheme: 2 - Fixed mounted dual secondary disconnect; Control Voltage: 6 - 48VDC; Application Card: 0 - Standard; Undervoltage: 0 - Undervoltage trip disabled; Button Color: 0 - Standard (ANSI); UL: 0 - None; Ground Contact: 1 - Standard fixed mount; Racking Mechanism: F - No Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
132048 | 3 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-03-25T00:00:00 | 2026-09-21T00:00:00 | 2026-07-20T00:00:00 | 3 | 0 | 3 | 32554.72 | 162773.6 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | AB4X3666XX000000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); X3 - 40.5kV, 3000A F.C., 25kA, 3 Cycle; CAP Switching: None; Charge Motor: 6 - 48VDC; Close Coil: 6 - 48VDC; Open Coil: 6 - 48VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - MANUAL TRUCK | PUR | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); X3 - 40.5kV, 3000A F.C., 25kA, 3 Cycle; CAP Switching: None; Charge Motor: 6 - 48VDC; Close Coil: 6 - 48VDC; Open Coil: 6 - 48VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - MANUAL TRUCK | EA | EA |  | TRUE |  | P | B/W | DAYTON
132048 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-25T00:00:00 | 2026-09-25T00:00:00 | 2026-07-13T00:00:00 | 6 | 0 | 6 | 8619.35 | 103432.2 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | 1YEC241980Z001 | Breaker compartment, 27kV@25kA, Epoxy 27kV 1200A. Upper/Lower position | PUR | Breaker compartment, 27kV@25kA, Epoxy 27kV 1200A. Upper/Lower position | EA | EA |  | TRUE |  | P | B/W | DAYTON | 2026-07-13T00:00:00
135300 | 2 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-08-07T00:00:00 | 2026-11-10T00:00:00 | 2026-11-10T00:00:00 | 14 | 0 | 14 | 1330 | 18620 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 4NWR002204 | IntraPack Part No.: F012384-A02, Secondary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black | PUR | IntraPack Part No.: F012384-A02, Secondary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black | EA | EA |  | TRUE |  | P | B/W | DAYTON
135300 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-08-07T00:00:00 | 2026-11-10T00:00:00 | 2026-11-10T00:00:00 | 2 | 0 | 2 | 2095 | 4190 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 4NWR002253 | IntraPack Part No.: F012382-A02, Standard Primary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black - Data logger provided by ABB | PUR | IntraPack Part No.: F012382-A02, Standard Primary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black - Data logger provided by ABB | EA | EA |  | TRUE |  | P | B/W | DAYTON
133430 | 21 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 6441.69 | 25766.76 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | UPS-FOBDEST | FCA Destination Charges Included | PUR | FCA Destination Charges Included | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 7 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 13880.48 | 55521.92 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | 79-5000-00000047 | 4000A DC Junction Cabinet: - NEMA-1 enclosure - Dim: 30"W x 24"D x 87"H - Front access; - Installed end cap of battery lineup closer to UPS I/O section - Accommodates up to 10 DC battery cabinet landings - Installed by contractor - see ABB installation drawing; | PUR | 4000A DC Junction Cabinet: - NEMA-1 enclosure - Dim: 30"W x 24"D x 87"H - Front access; - Installed end cap of battery lineup closer to UPS I/O section - Accommodates up to 10 DC battery cabinet landings - Installed by contractor - see ABB installation drawing; | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 6 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 3252.38 | 13009.52 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | 4NWR002253 | IntraPack Part No.: F012382-A02, Standard Primary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black - Data logger provided by ABB | PUR | IntraPack Part No.: F012382-A02, Standard Primary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black - Data logger provided by ABB | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 18 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 1300 | 10400 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE-8HR | Provide 8 hours response time ($1300/annual rate) | PUR | Provide 8 hours response time ($1300/annual rate) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 9 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 4000 | 32000 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | FREIGHT_RIC | Freight: Incoterm FCA Factory - Freight allowed | PUR | Freight: Incoterm FCA Factory - Freight allowed | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 22 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 5682.78 | 22731.12 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | UPS-FOBDEST_ | FCA Destination Charges Included | PUR | FCA Destination Charges Included | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 13 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | MOBILIZATION_UPS PKG | Mobilization for UPS Pkg (for L4/L5/L6T Tasks) | PUR | Mobilization for UPS Pkg (for L4/L5/L6T Tasks) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 17 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 4750 | 76000 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE Spec | Spec 263353.1, Par 3.2.B - Battery installation by UPS Manufacturer | PUR | Spec 263353.1, Par 3.2.B - Battery installation by UPS Manufacturer | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 12 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | MOBILIZATION_UPS | Mobilization for UPS Pkg (assume startup at same time for both UPS's) | PUR | Mobilization for UPS Pkg (assume startup at same time for both UPS's) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 1 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 1504.2 | 6016.8 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | 4NWA7000321568A | MegaFlex Seismic Bracket | PUR | MegaFlex Seismic Bracket | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 3 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 317079.24 | 1268316.96 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | 4NWP106511R0002 | MegaFlex 1.5MW UPS 480V 60Hz: Static Bypass - 100% rated continuous duty; Cabinet color: RAL 9005 (black); Single or dual AC feed; Short circuit withstand rating: 100kAIC; Input Voltage: 480V 3-Phase + Gnd , +/- 15% voltage tolerance, Frequency: 60Hz +/- 10%, PF = 0.99; Output: 480V, 3W + Gnd, Frequency: 60Hz & PF = 1.0; Efficiency: Up to 97% Double Conversion (VFI) & Up to 99% eBoost mode (VFD); Compatible Battery Technologies: LiB, NiZn, VRLA | PUR | MegaFlex 1.5MW UPS 480V 60Hz: Static Bypass - 100% rated continuous duty; Cabinet color: RAL 9005 (black); Single or dual AC feed; Short circuit withstand rating: 100kAIC; Input Voltage: 480V 3-Phase + Gnd , +/- 15% voltage tolerance, Frequency: 60Hz +/- 10%, PF = 0.99; Output: 480V, 3W + Gnd, Frequency: 60Hz & PF = 1.0; Efficiency: Up to 97% Double Conversion (VFI) & Up to 99% eBoost mode (VFD); Compatible Battery Technologies: LiB, NiZn, VRLA | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 2 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 32 | 0 | 32 | 31695.62 | 1014259.84 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | 4NWP104024R36U2, 8 LiBC/UPS | Samsung 136S Lithium Battery Cabinets/UPS: - High cycle / High Power Density - UL9540/UL9540A Listed - Top Cable Entry - DC Breaker in each battery cabinet - DIM/BC: 25.5 in W x 21 in D x 87 in H; - Approx Weight/BC: 1125 lbs - Battery runtime: 7 minn BOL / 5 min EOL for 1579 kWb battery loads | PUR | Samsung 136S Lithium Battery Cabinets/UPS: - High cycle / High Power Density - UL9540/UL9540A Listed - Top Cable Entry - DC Breaker in each battery cabinet - DIM/BC: 25.5 in W x 21 in D x 87 in H; - Approx Weight/BC: 1125 lbs - Battery runtime: 7 minn BOL / 5 min EOL for 1579 kWb battery loads | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 16 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 2 | 0 | 2 | 4750 | 9500 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE | Level-3 Startup: Additional startup time - interfacing with and checking of Maintenance Bypass Switchboards (not actual SU of MBC or MBS) | PUR | Level-3 Startup: Additional startup time - interfacing with and checking of Maintenance Bypass Switchboards (not actual SU of MBC or MBS) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 20 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | S-OST | Par 3.4.K - Onsite Training after startup/commissioning completion, contiguous US only (1 day / site + daily rate applied if exceeds) | PUR | Par 3.4.K - Onsite Training after startup/commissioning completion, contiguous US only (1 day / site + daily rate applied if exceeds) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 11 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 14250 | 57000 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | FSUMEG1600P1 | Level-3 Startup of MegaFlex UPS | PUR | Level-3 Startup of MegaFlex UPS | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 10 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 9500 | 38000 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | FSULITHI136X8P1 | Level-3 Startup of Lithium-Ion Batteries Note: Installation & connecting of batteries in the cabinets are by others (per adder above) | PUR | Level-3 Startup of Lithium-Ion Batteries Note: Installation & connecting of batteries in the cabinets are by others (per adder above) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 23 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 34500 | 138000 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | WARMEG-2.2 | Provide 2 year extended warranty with annual PM of UPS & batteries | PUR | Provide 2 year extended warranty with annual PM of UPS & batteries | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 14 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 4750 | 38000 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | S-CM1_UPS 3.5.B | Spec 263353, Par 3.5.B Level-4 Performance Testing per system Par 3.5.B: 2 days onsite (Deviate from 10 to 2 days per Customer Request) | PUR | Spec 263353, Par 3.5.B Level-4 Performance Testing per system Par 3.5.B: 2 days onsite (Deviate from 10 to 2 days per Customer Request) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 9 | 2 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 4000 | 32000 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | FREIGHT_RIC | Freight: Incoterm FCA Factory - Freight allowed | PUR | Freight: Incoterm FCA Factory - Freight allowed | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 15 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 4750 | 38000 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | S-CM1_UPS 3.5.D | (Customer to decide) Spec 263353, Par 3.5.D Level-4 Performance Testing per system Par 3.5.D: Exploratory period - 1st 2 days onsite Note: Customer to decide if this step is necessary | PUR | (Customer to decide) Spec 263353, Par 3.5.D Level-4 Performance Testing per system Par 3.5.D: Exploratory period - 1st 2 days onsite Note: Customer to decide if this step is necessary | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 8 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 1750.5 | 14004 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | 7GSP017351R0001 | UPS OPT IM0171E CUSTOMER INTERFAIEC_1605 | PUR | CIC Communication Card | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 5 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 28 | 0 | 28 | 1653.75 | 46305 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | 4NWR002204 | IntraPack Part No.: F012384-A02, Secondary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black | PUR | IntraPack Part No.: F012384-A02, Secondary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
133430 | 19 | 1 | States | Gardner Builders | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 4750 | 19000 | 55123 | USA | N45 | 1524 | ABB INC | 27511 | S-IST | (1 day/UPS is recommended) Spec 263353, Par 3.6A Level-5 Integration System Testing (IST) (1 day included + daily rate applied if exceeds) | PUR | (1 day/UPS is recommended) Spec 263353, Par 3.6A Level-5 Integration System Testing (IST) (1 day included + daily rate applied if exceeds) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077403-10-1
132140 | 2 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-03-30T00:00:00 | 2026-09-18T00:00:00 | 2026-06-26T00:00:00 | 2 | 0 | 2 | 1330.53 | 11974.77 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | CL1YBC0000000U | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: C - 19 Inch ODNWI Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: C - 19 Inch ODNWI Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
132140 | 3 | 3 | States | Dayton | Hayley Fabian | TRUE | 2026-03-30T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 68 | 0 | 68 | 2868.18 | 390072.48 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | VK3P2764N00CCR3000 | ABB 27kV VERSARUPTER - 600A,K MECH, VK3P2764N00CCR3000 | PUR | ABB 27kV VERSARUPTER - 600A,K MECH, VK3P2764N00CCR3000 | EA | EA |  | TRUE |  | P | B/W | DAYTON
132140 | 2 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-03-30T00:00:00 | 2026-09-18T00:00:00 | 2026-06-26T00:00:00 | 5 | 1 | 4 | 1330.53 | 11974.77 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | CL1YBC0000000U | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: C - 19 Inch ODNWI Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: C - 19 Inch ODNWI Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
132140 | 2 | 3 | States | Dayton | Hayley Fabian | TRUE | 2026-03-30T00:00:00 | 2026-09-18T00:00:00 | 2026-06-26T00:00:00 | 2 | 0 | 2 | 1330.53 | 11974.77 | 55369-6417 | USA | N60 | 1524 | ABB INC | 27511 | CL1YBC0000000U | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: C - 19 Inch ODNWI Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: C - 19 Inch ODNWI Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
133368 | 13 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 16 | 0 | 16 | 32030.92 | 672649.32 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | BA4JA777XX000U00 | ADVAC G; A - Drawout; J1 - 15kV, 1200A, 40kA; Charge Motor: 7 - 110-125VDC; Close Coil Voltage: 7 - 110-125VDC; Open Coil: 7 - 110-125VDC; Standard ABB Labels; Ground Contact: 0 – Lock Handle Kit; Motorized Truck: 0 – Manual Truck | PUR | ADVAC G; A - Drawout; J1 - 15kV, 1200A, 40kA; Charge Motor: 7 - 110-125VDC; Close Coil Voltage: 7 - 110-125VDC; Open Coil: 7 - 110-125VDC; Standard ABB Labels; Ground Contact: 0 – Lock Handle Kit; Motorized Truck: 0 – Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
133368 | 8 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-10-23T00:00:00 | 2026-10-23T00:00:00 | 12 | 1 | 11 | 451.93 | 12202.11 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 923A329G17-M | CURRENT TRANSFORMER SAB-1, INDOOR application, 10 kV BIL, Nominal system voltage: 0.6 kV, Primary current: 3000 Amps, Secondary current: 5 Amps, Rating factor: 1.33, Metering accuracy: 0.3B-1.8, Relay accuracy: C400, Frequency: 50-400 Hertz; | PUR | CURRENT TRANSFORMER SAB-1, INDOOR application, 10 kV BIL, Nominal system voltage: 0.6 kV, Primary current: 3000 Amps, Secondary current: 5 Amps, Rating factor: 1.33, Metering accuracy: 0.3B-1.8, Relay accuracy: C400, Frequency: 50-400 Hertz; | EA | EA |  | TRUE |  | P | B/W | Dayton
133368 | 4 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 10 | 0 | 10 | 3787.45 | 68174.1 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CP8A1W1NBY000U | Product Type: C - PT Compartment, Max Voltage: 15kV, Rated Voltage: 8 - 14.4 kV, Compartment Position: A - Position A, D, or E, Insulation Type: 1 - Polyester, Transformer Arrangement: W - (3) 1-Fuse Wye, Secondary Disconnect: 1 - With Secondary, PT and Fuse Equipment: N - Without PT and Fuse, Door Type: C - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - PT Compartment, Max Voltage: 15kV, Rated Voltage: 8 - 14.4 kV, Compartment Position: A - Position A, D, or E, Insulation Type: 1 - Polyester, Transformer Arrangement: W - (3) 1-Fuse Wye, Secondary Disconnect: 1 - With Secondary, PT and Fuse Equipment: N - Without PT and Fuse, Door Type: C - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
133368 | 1 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-12-07T00:00:00 | 2026-12-07T00:00:00 | 5 | 0 | 5 | 5364.48 | 48280.32 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 931868T01 | Breaker Lift Truck Assembly - manually operated | PUR | Breaker Lift Truck Assembly - manually operated | EA | EA |  | TRUE |  | P | B/W | DAYTON
133368 | 7 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-12-28T00:00:00 | 2026-12-28T00:00:00 | 4 | 0 | 4 | 414.72 | 6220.8 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 14039G00 | ADVAC Breaker Accessory Kit - racking crank, manual charging handle, & lift yoke | PUR | ADVAC Breaker Accessory Kit - racking crank, manual charging handle, & lift yoke | EA | EA |  | TRUE |  | P | B/W | Dayton
133368 | 13 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 5 | 0 | 5 | 32030.92 | 672649.32 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | BA4JA777XX000U00 | ADVAC G; A - Drawout; J1 - 15kV, 1200A, 40kA; Charge Motor: 7 - 110-125VDC; Close Coil Voltage: 7 - 110-125VDC; Open Coil: 7 - 110-125VDC; Standard ABB Labels; Ground Contact: 0 – Lock Handle Kit; Motorized Truck: 0 – Manual Truck | PUR | ADVAC G; A - Drawout; J1 - 15kV, 1200A, 40kA; Charge Motor: 7 - 110-125VDC; Close Coil Voltage: 7 - 110-125VDC; Open Coil: 7 - 110-125VDC; Standard ABB Labels; Ground Contact: 0 – Lock Handle Kit; Motorized Truck: 0 – Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
133368 | 4 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-12-28T00:00:00 | 2026-12-08T00:00:00 | 8 | 0 | 8 | 3787.45 | 68174.1 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CP8A1W1NBY000U | Product Type: C - PT Compartment, Max Voltage: 15kV, Rated Voltage: 8 - 14.4 kV, Compartment Position: A - Position A, D, or E, Insulation Type: 1 - Polyester, Transformer Arrangement: W - (3) 1-Fuse Wye, Secondary Disconnect: 1 - With Secondary, PT and Fuse Equipment: N - Without PT and Fuse, Door Type: C - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - PT Compartment, Max Voltage: 15kV, Rated Voltage: 8 - 14.4 kV, Compartment Position: A - Position A, D, or E, Insulation Type: 1 - Polyester, Transformer Arrangement: W - (3) 1-Fuse Wye, Secondary Disconnect: 1 - With Secondary, PT and Fuse Equipment: N - Without PT and Fuse, Door Type: C - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | DAYTON
133368 | 6 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-12-28T00:00:00 | 2026-12-28T00:00:00 | 4 | 0 | 4 | 1424.25 | 9969.75 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CL1YBY0000000U | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: B - 38 Inch MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: B - 38 Inch MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | dayton
133368 | 11 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 30 | 0 | 30 | 2272.49 | 122714.46 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 9629A02G10 | VIZ-11, INDOOR application, 110 kV BIL, Nominal system voltage: 15 kV, Connection type: LINE-GROUND, Primary voltage: 14400/14400GY Volts, Secondary voltage: 120 & 120, Metering accuracy: 0.3Y & 0.3Y, RVF: 1.1, Thermal rating: 1500, Frequency: 60 | PUR | VIZ-11, INDOOR application, 110 kV BIL, Nominal system voltage: 15 kV, Connection type: LINE-GROUND, Primary voltage: 14400/14400GY Volts, Secondary voltage: 120 & 120, Metering accuracy: 0.3Y & 0.3Y, RVF: 1.1, Thermal rating: 1500, Frequency: 60 | EA | EA |  | TRUE |  | P | B/W | DAYTON
133368 | 7 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 11 | 0 | 11 | 414.72 | 6220.8 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 14039G00 | ADVAC Breaker Accessory Kit - racking crank, manual charging handle, & lift yoke | PUR | ADVAC Breaker Accessory Kit - racking crank, manual charging handle, & lift yoke | EA | EA |  | TRUE |  | P | B/W | Dayton
133368 | 5 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 10 | 0 | 10 | 320 | 5760 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 965931T50 | PT drawer harness for dual secondary PT: Wye-Dela | PUR | PT drawer harness for dual secondary PT: Wye-Dela | EA | EA |  | TRUE |  | P | B/W | DAYTON
133368 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-11-30T00:00:00 | 2026-11-30T00:00:00 | 4 | 0 | 4 | 5364.48 | 48280.32 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 931868T01 | Breaker Lift Truck Assembly - manually operated | PUR | Breaker Lift Truck Assembly - manually operated | EA | EA |  | TRUE |  | P | B/W | DAYTON
133368 | 11 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-12-28T00:00:00 | 2026-12-28T00:00:00 | 24 | 0 | 24 | 2272.49 | 122714.46 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 9629A02G10 | VIZ-11, INDOOR application, 110 kV BIL, Nominal system voltage: 15 kV, Connection type: LINE-GROUND, Primary voltage: 14400/14400GY Volts, Secondary voltage: 120 & 120, Metering accuracy: 0.3Y & 0.3Y, RVF: 1.1, Thermal rating: 1500, Frequency: 60 | PUR | VIZ-11, INDOOR application, 110 kV BIL, Nominal system voltage: 15 kV, Connection type: LINE-GROUND, Primary voltage: 14400/14400GY Volts, Secondary voltage: 120 & 120, Metering accuracy: 0.3Y & 0.3Y, RVF: 1.1, Thermal rating: 1500, Frequency: 60 | EA | EA |  | TRUE |  | P | B/W | DAYTON
133368 | 10 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-12-28T00:00:00 | 2026-12-28T00:00:00 | 12 | 8 | 4 | 410.47 | 11082.69 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 923A329G15-M | Feeder, Current Transformer, 2000:5A Single Ratio Donut type Class 200 | PUR | Feeder, Current Transformer, 2000:5A Single Ratio Donut type Class 200 | EA | EA |  | TRUE |  | P | B/W | Dayton
133368 | 6 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 3 | 0 | 3 | 1424.25 | 9969.75 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CL1YBY0000000U | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: B - 38 Inch MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - LV Compartment, Compartment Height: 1 - 19 Inch, Bottom IT Pans: Y - Yes, Door Type: B - 38 Inch MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | dayton
133368 | 5 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-05-18T00:00:00 | 2026-12-28T00:00:00 | 2026-12-28T00:00:00 | 8 | 0 | 8 | 320 | 5760 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 965931T50 | PT drawer harness for dual secondary PT: Wye-Dela | PUR | PT drawer harness for dual secondary PT: Wye-Dela | EA | EA |  | TRUE |  | P | B/W | DAYTON
132210 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-01T00:00:00 | 2026-11-19T00:00:00 | 2026-11-19T00:00:00 | 10 | 0 | 10 | 5406.51 | 54065.1 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | BTO ATS 400A-600A | ZGDK3XX12-CX2XT4XX Automatic Transfer Switch, ZTG T-Series, 400 A-600 A "ZTG DT 400A3PH No Neu N1 General Purpose Commercial and Industrial Automatic Transfer Switch 400 A, 3 Phase (3 Pole), Delayed Transition NEMA 1 Enclosure 4 NO (Normally Open) and 4 NC (Normally Closed) Auxiliary Contacts No Neutral No Meters GB2 - (6)#8-1/0 Ground Bar Modbus TCP communications Additional 4 I/O, programmable T1-Panel Voltage agnostic, Rated for 200 to 480V line to line voltage Standard Application-Sources on Bottom UL 1008 listed up To 480VAC at 50/60Hz Seismic certified To IEEE-693-2005 at HIGH level With 2.5 amplification factor Seismic certified To IBC-2015 at Ip=1.5 For z/h less than Or equal To 1 Microprocessor activated Momentary test switch Programmable exerciser daily, 7-14-28-365 days user- selectable, with or without load Event log of last 250 events Adjustable over/under frequency sensor-Source 2-and Source 1 Frequency Indication - on the controller LED Source -2 - Position indication LED Source -1 - Position indication LED Source -2 - Source availability indication LED Source -1 - Source availability indication" "Engine start timer -adjustable up to 60sec Phase rotation sensing of Source 1 and Source 2 Under voltage sensing 3-phase Source 2 In Phase Monitor between Source 1 and Source 2 to allow transfer-with enable/disable Over voltage sensing-3 phase Source 2 Microprocessor activated Commit/no commit on transferring to Source 2-with enable/disable Time Delay from Neutral Position to Source 1 on Retransfer Time Delay from Neutral Position to Source 2 on Retransfer. Adjustable time delay on transfer to Source 1 Engine stop/cool adjustable cool down timer Voltage imbalance between phases-applies to 3-phase only Adjustable time delay on transfer to Source 2 Bypass transfer timer function-soft switch in controller Programmable Input Modules: (Must be configured by user upon installation) E-Stop Remote Control to S1 (R15 Load Shed) Remote Control to S2 Remote Control to OFF (R15D Load Shed) Inhibit Transfer Manual-Auto Mode Programmable Output Modules: (Must be configured by user upon installation) Alarm / Product Availability Load Connected to S1 Load Disconnected Load Connected to S2 Elevator Pre-transfer Signal (T3/W3)" | PUR | "Category: --- LV - Other --- Identifier: --- BTO ATS 400A-600A ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | Dayton
133425 | 1 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 1504.2 | 6016.8 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | 4NWA7000321568A | MegaFlex Seismic Bracket | PUR | MegaFlex Seismic Bracket | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 21 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 6441.69 | 25766.76 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | UPS-FOBDEST | FCA Destination Charges Included | PUR | FCA Destination Charges Included | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 10 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 9500 | 38000 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | FSULITHI136X8P1 | Level-3 Startup of Lithium-Ion Batteries Note: Installation & connecting of batteries in the cabinets are by others (per adder above) | PUR | Level-3 Startup of Lithium-Ion Batteries Note: Installation & connecting of batteries in the cabinets are by others (per adder above) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 23 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 34500 | 138000 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | WARMEG-2.2 | Provide 2 year extended warranty with annual PM of UPS & batteries | PUR | Provide 2 year extended warranty with annual PM of UPS & batteries | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 13 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | MOBILIZATION_UPS PKG | Mobilization for UPS Pkg (for L4/L5/L6T Tasks) | PUR | Mobilization for UPS Pkg (for L4/L5/L6T Tasks) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 6 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 3252.38 | 13009.52 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | 4NWR002253 | IntraPack Part No.: F012382-A02, Standard Primary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black - Data logger provided by ABB | PUR | IntraPack Part No.: F012382-A02, Standard Primary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black - Data logger provided by ABB | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 5 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 28 | 0 | 28 | 1653.75 | 46305 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | 4NWR002204 | IntraPack Part No.: F012384-A02, Secondary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black | PUR | IntraPack Part No.: F012384-A02, Secondary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 7 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 13880.48 | 55521.92 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | 79-5000-00000047 | 4000A DC Junction Cabinet: - NEMA-1 enclosure - Dim: 30"W x 24"D x 87"H - Front access; - Installed end cap of battery lineup closer to UPS I/O section - Accommodates up to 10 DC battery cabinet landings - Installed by contractor - see ABB installation drawing; | PUR | 4000A DC Junction Cabinet: - NEMA-1 enclosure - Dim: 30"W x 24"D x 87"H - Front access; - Installed end cap of battery lineup closer to UPS I/O section - Accommodates up to 10 DC battery cabinet landings - Installed by contractor - see ABB installation drawing; | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 11 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 14250 | 57000 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | FSUMEG1600P1 | Level-3 Startup of MegaFlex UPS | PUR | Level-3 Startup of MegaFlex UPS | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 15 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 8 | 0 | 8 | 4750 | 38000 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | S-CM1_UPS 3.5.D | (Customer to decide) Spec 263353, Par 3.5.D Level-4 Performance Testing per system Par 3.5.D: Exploratory period - 1st 2 days onsite Note: Customer to decide if this step is necessary | PUR | (Customer to decide) Spec 263353, Par 3.5.D Level-4 Performance Testing per system Par 3.5.D: Exploratory period - 1st 2 days onsite Note: Customer to decide if this step is necessary | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 14 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 8 | 0 | 8 | 4750 | 38000 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | S-CM1_UPS 3.5.B | Spec 263353, Par 3.5.B Level-4 Performance Testing per system Par 3.5.B: 2 days onsite (Deviate from 10 to 2 days per Customer Request) | PUR | Spec 263353, Par 3.5.B Level-4 Performance Testing per system Par 3.5.B: 2 days onsite (Deviate from 10 to 2 days per Customer Request) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 4 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 1864.75 | 7459 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | 4NWPN7574R0001 | Data Logger (w/o top hat), provided by ABB to be installed by IntraPack in the Primary Top hat | PUR | Data Logger (w/o top hat), provided by ABB to be installed by IntraPack in the Primary Top hat | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 9 | 2 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 4000 | 32000 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | FREIGHT_RIC | Freight: Incoterm FCA Factory - Freight allowed | PUR | Freight: Incoterm FCA Factory - Freight allowed | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 8 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 8 | 0 | 8 | 1750.5 | 14004 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | 7GSP017351R0001 | UPS OPT IM0171E CUSTOMER INTERFAIEC_1605 | PUR | CIC Communication Card | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 3 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 317079.24 | 1268316.96 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | 4NWP106511R0002 | MegaFlex 1.5MW UPS 480V 60Hz: Static Bypass - 100% rated continuous duty; Cabinet color: RAL 9005 (black); Single or dual AC feed; Short circuit withstand rating: 100kAIC; Input Voltage: 480V 3-Phase + Gnd , +/- 15% voltage tolerance, Frequency: 60Hz +/- 10%, PF = 0.99; Output: 480V, 3W + Gnd, Frequency: 60Hz & PF = 1.0; Efficiency: Up to 97% Double Conversion (VFI) & Up to 99% eBoost mode (VFD); Compatible Battery Technologies: LiB, NiZn, VRLA | PUR | MegaFlex 1.5MW UPS 480V 60Hz: Static Bypass - 100% rated continuous duty; Cabinet color: RAL 9005 (black); Single or dual AC feed; Short circuit withstand rating: 100kAIC; Input Voltage: 480V 3-Phase + Gnd , +/- 15% voltage tolerance, Frequency: 60Hz +/- 10%, PF = 0.99; Output: 480V, 3W + Gnd, Frequency: 60Hz & PF = 1.0; Efficiency: Up to 97% Double Conversion (VFI) & Up to 99% eBoost mode (VFD); Compatible Battery Technologies: LiB, NiZn, VRLA | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 17 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 16 | 0 | 16 | 4750 | 76000 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE Spec | Spec 263353.1, Par 3.2.B - Battery installation by UPS Manufacturer | PUR | Spec 263353.1, Par 3.2.B - Battery installation by UPS Manufacturer | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 20 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | S-OST | Par 3.4.K - Onsite Training after startup/commissioning completion, contiguous US only (1 day / site + daily rate applied if exceeds) | PUR | Par 3.4.K - Onsite Training after startup/commissioning completion, contiguous US only (1 day / site + daily rate applied if exceeds) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 16 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 2 | 0 | 2 | 4750 | 9500 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE | Level-3 Startup: Additional startup time - interfacing with and checking of Maintenance Bypass Switchboards (not actual SU of MBC or MBS) | PUR | Level-3 Startup: Additional startup time - interfacing with and checking of Maintenance Bypass Switchboards (not actual SU of MBC or MBS) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 2 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 32 | 0 | 32 | 31695.62 | 1014259.84 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | 4NWP104024R36U2, 8 LiBC/UPS | Samsung 136S Lithium Battery Cabinets/UPS: - High cycle / High Power Density - UL9540/UL9540A Listed - Top Cable Entry - DC Breaker in each battery cabinet - DIM/BC: 25.5 in W x 21 in D x 87 in H; - Approx Weight/BC: 1125 lbs - Battery runtime: 7 minn BOL / 5 min EOL for 1579 kWb battery loads | PUR | Samsung 136S Lithium Battery Cabinets/UPS: - High cycle / High Power Density - UL9540/UL9540A Listed - Top Cable Entry - DC Breaker in each battery cabinet - DIM/BC: 25.5 in W x 21 in D x 87 in H; - Approx Weight/BC: 1125 lbs - Battery runtime: 7 minn BOL / 5 min EOL for 1579 kWb battery loads | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 9 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 4000 | 32000 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | FREIGHT_RIC | Freight: Incoterm FCA Factory - Freight allowed | PUR | Freight: Incoterm FCA Factory - Freight allowed | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 19 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 4750 | 19000 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | S-IST | (1 day/UPS is recommended) Spec 263353, Par 3.6A Level-5 Integration System Testing (IST) (1 day included + daily rate applied if exceeds) | PUR | (1 day/UPS is recommended) Spec 263353, Par 3.6A Level-5 Integration System Testing (IST) (1 day included + daily rate applied if exceeds) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 18 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 8 | 0 | 8 | 1300 | 10400 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE-8HR | Provide 8 hours response time ($1300/annual rate) | PUR | Provide 8 hours response time ($1300/annual rate) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 12 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | MOBILIZATION_UPS | Mobilization for UPS Pkg (assume startup at same time for both UPS's) | PUR | Mobilization for UPS Pkg (assume startup at same time for both UPS's) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
133425 | 22 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 5682.78 | 22731.12 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | UPS-FOBDEST_ | FCA Destination Charges Included | PUR | FCA Destination Charges Included | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-11-1
132286 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-07T00:00:00 | 2026-12-22T00:00:00 | 2026-12-22T00:00:00 | 1 | 0 | 1 | 22200 | 22200 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | Level 4 & 5 Onsite testing for ABB UPS & STS | Category: --- Identifier: --- Level 4 & 5 Onsite testing for ABB UPS & STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | PUR | "Category: --- Identifier: --- Level 4 & 5 Onsite testing for ABB UPS & STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W
135878 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-09-02T00:00:00 | 2027-01-18T00:00:00 | 2027-01-18T00:00:00 | 11 | 0 | 11 | 469.24 | 5161.64 | 55369 | USA | N45 | 1524 | ABB INC | 27511 | 244006516 | Auxiliary switch, 6 contacts, for 4.76-27 kV | MVMS | Auxiliary switch, 6 contacts, for 4.76-27 kV | EA | EA |  | TRUE |  | P | B/W | Dayton
133586 | 5 | 1 | States | Oppidan Ashland | Hayley Fabian | TRUE | 2026-05-22T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 4 | 0 | 4 | 4255 | 17020 | 23005 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Level 4 | Level 4 Performancy Testing - (4) Days(s) | PUR | Level 4 Performancy Testing - (4) Days(s) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077406-13-1
133586 | 1 | 1 | States | Oppidan Ashland | Hayley Fabian | TRUE | 2026-05-22T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 24 | 0 | 24 | 95892 | 2301408 | 23005 | USA | N45 | 1524 | ABB INC | 27511 | SuperSwitch 4 (DSTS) | 1200A, 480V, DSTS (SS4) | PUR | 1200A, 480V, DSTS (SS4) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077406-13-1
133586 | 9 | 1 | States | Oppidan Ashland | Hayley Fabian | TRUE | 2026-05-22T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 1 | 0 | 1 | 130100 | 130100 | 23005 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - Extended Warranty | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | PUR | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077406-13-1
133586 | 3 | 1 | States | Oppidan Ashland | Hayley Fabian | TRUE | 2026-05-22T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 24 | 0 | 24 | 390 | 9360 | 23005 | USA | N45 | 1524 | ABB INC | 27511 | 800A-1200A Vented Kickplates | SuperSwitch 4 - 800A-1200A Vented Kickplates | PUR | SuperSwitch 4 - 800A-1200A Vented Kickplates | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077406-13-1
133586 | 2 | 1 | States | Oppidan Ashland | Hayley Fabian | TRUE | 2026-05-22T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 24 | 0 | 24 | 10243 | 245832 | 23005 | USA | N45 | 1524 | ABB INC | 27511 | 1200A 24" Front Access Sidecar | SuperSwitch 4 - 1200A 24" Front Access Sidecar | PUR | SuperSwitch 4 - 1200A 24" Front Access Sidecar | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077406-13-1
133586 | 7 | 1 | States | Oppidan Ashland | Hayley Fabian | TRUE | 2026-05-22T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 3 | 0 | 3 | 4500 | 13500 | 23005 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Mobilization | Mobilization - (3) Visit(s) | PUR | Mobilization - (3) Visit(s) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077406-13-1
133586 | 4 | 1 | States | Oppidan Ashland | Hayley Fabian | TRUE | 2026-05-22T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 12 | 0 | 12 | 4450 | 53400 | 23005 | USA | N45 | 1524 | ABB INC | 27511 | Services - Start-up Service | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | PUR | On-site Service Per Day (not to exceed 12 days), M-F 8am-5pm | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077406-13-1
133586 | 8 | 1 | States | Oppidan Ashland | Hayley Fabian | TRUE | 2026-05-22T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 144 | 0 | 144 | 57 | 8208 | 23005 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - STS | STS Pedestals | PUR | STS Pedestals | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077406-13-1
133586 | 6 | 1 | States | Oppidan Ashland | Hayley Fabian | TRUE | 2026-05-22T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 1 | 0 | 1 | 4255 | 4255 | 23005 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Integration Testing | Integration Testing - (1) Day(s) | PUR | Integration Testing - (1) Day(s) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077406-13-1
132285 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-04-07T00:00:00 | 2026-12-22T00:00:00 | 2026-12-22T00:00:00 | 1 | 0 | 1 | 22200 | 22200 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | Level 4 & 5 Onsite testing for ABB UPS & STS | Category: --- Identifier: --- Level 4 & 5 Onsite testing for ABB UPS & STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | PUR | "Category: --- Identifier: --- Level 4 & 5 Onsite testing for ABB UPS & STS ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W
135099 | 3 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-29T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 1 | 0 | 1 | 8367.18 | 8367.18 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VCF549716R0005 | KIT 10 MOUNTING HEART + AUXILIARY | Buy | KIT 10 MOUNTING HEART + AUXILIARY | EA | EA |  | TRUE |  | P | B/W | DAYTON | 2026-09-30T00:00:00
135099 | 2 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-29T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 1 | 0 | 1 | 5787.78 | 5787.78 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VCF549716R0001 | KIT 10+10 LEFT AND RIGHT RAILS PB8 | Buy | KIT 10+10 LEFT AND RIGHT RAILS PB8 | EA | EA |  | TRUE |  | P | B/W | DAYTON | 2026-09-30T00:00:00
135099 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-29T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 1 | 0 | 1 | 6742.71 | 6742.71 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VCF549716R0006 | KIT 10 WIRING TABLE AUX CONTACT 38 KV | Buy | KIT 10 WIRING TABLE AUX CONTACT 38 KV | EA | EA |  | TRUE |  | P | B/W | DAYTON | 2026-09-30T00:00:00
133434 | 21 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 6441.69 | 25766.76 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | UPS-FOBDEST | FCA Destination Charges Included | PUR | FCA Destination Charges Included | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 4 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 1864.75 | 7459 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | 4NWPN7574R0001 | Data Logger (w/o top hat), provided by ABB to be installed by IntraPack in the Primary Top hat | PUR | Data Logger (w/o top hat), provided by ABB to be installed by IntraPack in the Primary Top hat | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 18 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 1300 | 10400 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE-8HR | Provide 8 hours response time ($1300/annual rate) | PUR | Provide 8 hours response time ($1300/annual rate) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 2 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 32 | 0 | 32 | 31695.62 | 1014259.84 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | 4NWP104024R36U2, 8 LiBC/UPS | Samsung 136S Lithium Battery Cabinets/UPS: - High cycle / High Power Density - UL9540/UL9540A Listed - Top Cable Entry - DC Breaker in each battery cabinet - DIM/BC: 25.5 in W x 21 in D x 87 in H; - Approx Weight/BC: 1125 lbs - Battery runtime: 7 minn BOL / 5 min EOL for 1579 kWb battery loads | PUR | Samsung 136S Lithium Battery Cabinets/UPS: - High cycle / High Power Density - UL9540/UL9540A Listed - Top Cable Entry - DC Breaker in each battery cabinet - DIM/BC: 25.5 in W x 21 in D x 87 in H; - Approx Weight/BC: 1125 lbs - Battery runtime: 7 minn BOL / 5 min EOL for 1579 kWb battery loads | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 20 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | S-OST | Par 3.4.K - Onsite Training after startup/commissioning completion, contiguous US only (1 day / site + daily rate applied if exceeds) | PUR | Par 3.4.K - Onsite Training after startup/commissioning completion, contiguous US only (1 day / site + daily rate applied if exceeds) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 10 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 9500 | 38000 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | FSULITHI136X8P1 | Level-3 Startup of Lithium-Ion Batteries Note: Installation & connecting of batteries in the cabinets are by others (per adder above) | PUR | Level-3 Startup of Lithium-Ion Batteries Note: Installation & connecting of batteries in the cabinets are by others (per adder above) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 5 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 28 | 0 | 28 | 1653.75 | 46305 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | 4NWR002204 | IntraPack Part No.: F012384-A02, Secondary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black | PUR | IntraPack Part No.: F012384-A02, Secondary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 11 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 14250 | 57000 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | FSUMEG1600P1 | Level-3 Startup of MegaFlex UPS | PUR | Level-3 Startup of MegaFlex UPS | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 16 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 2 | 0 | 2 | 4750 | 9500 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE | Level-3 Startup: Additional startup time - interfacing with and checking of Maintenance Bypass Switchboards (not actual SU of MBC or MBS) | PUR | Level-3 Startup: Additional startup time - interfacing with and checking of Maintenance Bypass Switchboards (not actual SU of MBC or MBS) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 22 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 5682.78 | 22731.12 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | UPS-FOBDEST_ | FCA Destination Charges Included | PUR | FCA Destination Charges Included | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 19 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 4750 | 19000 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | S-IST | (1 day/UPS is recommended) Spec 263353, Par 3.6A Level-5 Integration System Testing (IST) (1 day included + daily rate applied if exceeds) | PUR | (1 day/UPS is recommended) Spec 263353, Par 3.6A Level-5 Integration System Testing (IST) (1 day included + daily rate applied if exceeds) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 23 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 34500 | 138000 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | WARMEG-2.2 | Provide 2 year extended warranty with annual PM of UPS & batteries | PUR | Provide 2 year extended warranty with annual PM of UPS & batteries | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 12 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | MOBILIZATION_UPS | Mobilization for UPS Pkg (assume startup at same time for both UPS's) | PUR | Mobilization for UPS Pkg (assume startup at same time for both UPS's) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 3 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 317079.24 | 1268316.96 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | 4NWP106511R0002 | MegaFlex 1.5MW UPS 480V 60Hz: Static Bypass - 100% rated continuous duty; Cabinet color: RAL 9005 (black); Single or dual AC feed; Short circuit withstand rating: 100kAIC; Input Voltage: 480V 3-Phase + Gnd , +/- 15% voltage tolerance, Frequency: 60Hz +/- 10%, PF = 0.99; Output: 480V, 3W + Gnd, Frequency: 60Hz & PF = 1.0; Efficiency: Up to 97% Double Conversion (VFI) & Up to 99% eBoost mode (VFD); Compatible Battery Technologies: LiB, NiZn, VRLA | PUR | MegaFlex 1.5MW UPS 480V 60Hz: Static Bypass - 100% rated continuous duty; Cabinet color: RAL 9005 (black); Single or dual AC feed; Short circuit withstand rating: 100kAIC; Input Voltage: 480V 3-Phase + Gnd , +/- 15% voltage tolerance, Frequency: 60Hz +/- 10%, PF = 0.99; Output: 480V, 3W + Gnd, Frequency: 60Hz & PF = 1.0; Efficiency: Up to 97% Double Conversion (VFI) & Up to 99% eBoost mode (VFD); Compatible Battery Technologies: LiB, NiZn, VRLA | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 13 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 1 | 0 | 1 | 4750 | 4750 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | MOBILIZATION_UPS PKG | Mobilization for UPS Pkg (for L4/L5/L6T Tasks) | PUR | Mobilization for UPS Pkg (for L4/L5/L6T Tasks) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 17 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 16 | 0 | 16 | 4750 | 76000 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | SERVICEFLATRATE Spec | Spec 263353.1, Par 3.2.B - Battery installation by UPS Manufacturer | PUR | Spec 263353.1, Par 3.2.B - Battery installation by UPS Manufacturer | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 14 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 4750 | 38000 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | S-CM1_UPS 3.5.B | Spec 263353, Par 3.5.B Level-4 Performance Testing per system Par 3.5.B: 2 days onsite (Deviate from 10 to 2 days per Customer Request) | PUR | Spec 263353, Par 3.5.B Level-4 Performance Testing per system Par 3.5.B: 2 days onsite (Deviate from 10 to 2 days per Customer Request) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 6 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 3252.38 | 13009.52 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | 4NWR002253 | IntraPack Part No.: F012382-A02, Standard Primary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black - Data logger provided by ABB | PUR | IntraPack Part No.: F012382-A02, Standard Primary top hat, Samsung Lithium-Ion UL9540A battery cabinet includes: - Cable management for Positive, Negative and Frame Ground Cables - Removable Front and Top Gland Plates - Paint color: Black - Data logger provided by ABB | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 8 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 1750.5 | 14004 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | 7GSP017351R0001 | UPS OPT IM0171E CUSTOMER INTERFAIEC_1605 | PUR | CIC Communication Card | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 9 | 2 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 4000 | 32000 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | FREIGHT_RIC | Freight: Incoterm FCA Factory - Freight allowed | PUR | Freight: Incoterm FCA Factory - Freight allowed | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 9 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 4000 | 32000 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | FREIGHT_RIC | Freight: Incoterm FCA Factory - Freight allowed | PUR | Freight: Incoterm FCA Factory - Freight allowed | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 1 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 1504.2 | 6016.8 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | 4NWA7000321568A | MegaFlex Seismic Bracket | PUR | MegaFlex Seismic Bracket | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 15 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 8 | 0 | 8 | 4750 | 38000 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | S-CM1_UPS 3.5.D | (Customer to decide) Spec 263353, Par 3.5.D Level-4 Performance Testing per system Par 3.5.D: Exploratory period - 1st 2 days onsite Note: Customer to decide if this step is necessary | PUR | (Customer to decide) Spec 263353, Par 3.5.D Level-4 Performance Testing per system Par 3.5.D: Exploratory period - 1st 2 days onsite Note: Customer to decide if this step is necessary | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
133434 | 7 | 1 | States | Whiting Turner | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-06-30T00:00:00 | 2027-06-30T00:00:00 | 4 | 0 | 4 | 13880.48 | 55521.92 | 68138 | USA | N45 | 1524 | ABB INC | 27511 | 79-5000-00000047 | 4000A DC Junction Cabinet: - NEMA-1 enclosure - Dim: 30"W x 24"D x 87"H - Front access; - Installed end cap of battery lineup closer to UPS I/O section - Accommodates up to 10 DC battery cabinet landings - Installed by contractor - see ABB installation drawing; | PUR | 4000A DC Junction Cabinet: - NEMA-1 enclosure - Dim: 30"W x 24"D x 87"H - Front access; - Installed end cap of battery lineup closer to UPS I/O section - Accommodates up to 10 DC battery cabinet landings - Installed by contractor - see ABB installation drawing; | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077405-11-1
134626 | 7 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 252 | 0 | 252 | 114.7 | 28904.4 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 2RKA024750A0001 | Adapter plate for KECA 80 current sensor | PUR | Adapter plate for KECA 80 current sensor | EA | EA |  | TRUE |  | P | B/W | DAYTON
134626 | 8 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 84 | 0 | 84 | 273.4 | 22965.6 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VL5300817R0102 | AR5 adapter 3x female RJ45 to 6x female RJ45 | PUR | AR5 adapter 3x female RJ45 to 6x female RJ45 | EA | EA |  | TRUE |  | P | B/W | DAYTON
134626 | 3 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 16 | 0 | 16 | 36746.53 | 587944.48 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AB4Z2777XX000000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z2 - 40.5kV, 2000A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | PUR | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z2 - 40.5kV, 2000A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | DAYTON
134626 | 5 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 234 | 0 | 234 | 898.49 | 210246.66 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VL5400072V1202 | Current Sensors | PUR | Current Sensors | EA | EA |  | TRUE |  | P | B/W | DAYTON
134626 | 4 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 16 | 0 | 16 | 20611.33 | 329781.28 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CBRL24221AY000 | Product Type: CB - Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 2 - 2000 A, Short Circuit Current: 4 - 40 kA, CTs Kits: 2 - 12 CTs per compartment, TOC Harness: 1 - 8 Contacts, Door Type: A - RH Door, Door Stop: Y - Yes, SmartRack: 0 - None | PUR | Product Type: CB - Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 2 - 2000 A, Short Circuit Current: 4 - 40 kA, CTs Kits: 2 - 12 CTs per compartment, TOC Harness: 1 - 8 Contacts, Door Type: A - RH Door, Door Stop: Y - Yes, SmartRack: 0 - None | EA | EA |  | TRUE |  | P | B/W | DAYTON
134626 | 6 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 297 | 0 | 297 | 2363.94 | 702090.18 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VL5400086V1304 | Voltage Sensors | PUR | Voltage Sensors | EA | EA |  | TRUE |  | P | B/W | DAYTON
134626 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 16 | 0 | 16 | 31390.85 | 1820669.3 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AB4Z1777XX000000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | MVMS | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | Dayton
134626 | 2 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 57 | 0 | 57 | 20611.33 | 1174845.81 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CBRL14221AY000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Product Type: CB - Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 4 - 40 kA, CTs Kits: 2 - 12 CTs per compartment, TOC Harness: 1 - 8 Contacts, Door Type: A - RH Door, Door Stop: Y - Yes, SmartRack: 0 - None | PUR | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Product Type: CB - Breaker Compartment, Cell Interface: R - Roll On Floor, Types Rating: L - 38 kV, Bushing Type: 1 - 1200 A, Short Circuit Current: 4 - 40 kA, CTs Kits: 2 - 12 CTs per compartment, TOC Harness: 1 - 8 Contacts, Door Type: A - RH Door, Door Stop: Y - Yes, SmartRack: 0 - None | EA | EA |  | TRUE |  | P | B/W | Dayton
134626 | 10 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 240 | 0 | 240 | 114.7 | 27528 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VL5300752R1102 | AR4 red adapter 2.2m, I+U with 2x female RJ45 to 1 male RJ45 | PUR | AR4 red adapter 2.2m, I+U with 2x female RJ45 to 1 male RJ45 | EA | EA |  | TRUE |  | P | B/W | DAYTON
134626 | 9 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 16 | 0 | 16 | 2081.2 | 33299.2 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VL5400180V1116 | Voltage sensor with red/black ferruled cable connections. 31.5/√3 kV, 2 MΩ/50 pF | PUR | Voltage sensor with red/black ferruled cable connections. 31.5/√3 kV, 2 MΩ/50 pF | EA | EA |  | TRUE |  | P | B/W | DAYTON
134626 | 1 | 2 | States | Dayton | Hayley Fabian | TRUE | 2026-07-10T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 42 | 0 | 42 | 31390.85 | 1820669.3 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | AB4Z1777XX000000 | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | MVMS | ADVAC38; 4 - Model 4; B - Roll on Floor (ROF); Z1 - 40.5kV, 1200A, 40kA, 3 Cycle; CAP Switching: 1000A C2 20kA PEAK 4.3 kHz; Charge Motor: 7 - 125VDC; Close Coil: 7 - 125VDC; Open Coil: 7 - 125VDC; 2nd Open Coil: X - None (Dual Secondary Disconnect); Under Voltage: X - None (Dual Secondary Disconnect); Button Color: 0 - None; Button Protection: 0 - None; UL: 0 - None; Ground Contact: 0 - Ground pad stainless steel; Motor Truck: 0 - Manual Truck | EA | EA |  | TRUE |  | P | B/W | Dayton
135100 | 4 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-08-04T00:00:00 | 2026-10-13T00:00:00 | 2026-10-13T00:00:00 | 3 | 0 | 3 | 1490.95 | 4472.85 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VL5400152V1116 | KEVA 24 B21 Voltage Sensor 200 kO/350 pF 9.9m Cable | PUR | KEVA 24 B21 Voltage Sensor 200 kO/350 pF 9.9m Cable | EA | EA |  | TRUE |  | P | B/W | DAYTON
135100 | 2 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-08-04T00:00:00 | 2026-10-27T00:00:00 | 2026-10-27T00:00:00 | 1 | 0 | 1 | 9463.52 | 9463.52 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 1VCF549700R0580 | BREAKER LIFT TRUCK 38KV ADVAC | PUR | BREAKER LIFT TRUCK 38KV ADVAC | EA | EA |  | TRUE |  | P | B/W | DAYTON
135100 | 1 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-08-04T00:00:00 | 2026-11-04T00:00:00 | 2026-11-04T00:00:00 | 1 | 0 | 1 | 354.6 | 354.6 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | 95A1159G02 | FT-14D test harness, Quantity 3 (kit for 3-phase testing) | PUR | FT-14D test harness, Quantity 3 (kit for 3-phase testing) | EA | EA |  | TRUE |  | P | B/W | DAYTON
135100 | 3 | 1 | States | Dayton | Hayley Fabian | TRUE | 2026-08-04T00:00:00 | 2026-11-17T00:00:00 | 2026-11-17T00:00:00 | 2 | 0 | 2 | 5296.1 | 10592.2 | 55369-6417 | USA | N45 | 1524 | ABB INC | 27511 | CB11L1211BY00U | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: L - Lower, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | PUR | Product Type: C - Breaker Compartment, Cell Interface: 1 - Standard Drawout, Types Rating: 1 - 5-15kV@50kA, Compartment Position: L - Lower, Bushing Type: 1 - Polyester - 1200A, Secondary Disconnect: 2 - Dual, Shutter Type: 1 - Grounded Metal, TOC Harness: 1 - 8 Contacts, Door Type: B - MPL Assembly, Door Stop: Y - Yes, Qualification: U - UL Recognized | EA | EA |  | TRUE |  | P | B/W | dayton
133443 | 4 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 4 | 0 | 4 | 4255 | 17020 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Level 4 | Level 4 Performancy Testing - (4) Days(s) | PUR | Level 4 Performancy Testing - (4) Days(s) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-12-1
133443 | 7 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 16 | 0 | 16 | 95892 | 1534272 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | SuperSwitch 4 (DSTS) | 1200A, 480V, DSTS (SS4) | PUR | 1200A, 480V, DSTS (SS4) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-12-1
133443 | 5 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 3 | 0 | 3 | 4500 | 13500 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Mobilization | Mobilization - (3) Visit(s) | PUR | Mobilization - (3) Visit(s) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-12-1
133443 | 6 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 8 | 0 | 8 | 4450 | 35600 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | Services - Start-up Service | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | PUR | On-site Service Per Day (not to exceed 3 days), M-F 8am-5pm | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-12-1
133443 | 3 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 1 | 0 | 1 | 4255 | 4255 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | Other Services - Integration Testing | Integration Testing - (1) Day(s) | PUR | Integration Testing - (1) Day(s) | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-12-1
133443 | 1 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 16 | 0 | 16 | 10243 | 163888 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | 1200A 24" Front Access Sidecar | SuperSwitch 4 - 1200A 24" Front Access Sidecar | PUR | SuperSwitch 4 - 1200A 24" Front Access Sidecar | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-12-1
133443 | 8 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 96 | 0 | 96 | 57 | 5472 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - STS | STS Pedestals | PUR | STS Pedestals | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-12-1
133443 | 2 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 16 | 0 | 16 | 390 | 6240 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | 800A-1200A Vented Kickplates | SuperSwitch 4 - 800A-1200A Vented Kickplates | PUR | SuperSwitch 4 - 800A-1200A Vented Kickplates | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-12-1
133443 | 9 | 1 | States | EE Reed | Hayley Fabian | TRUE | 2026-05-20T00:00:00 | 2027-09-30T00:00:00 | 2027-09-30T00:00:00 | 1 | 0 | 1 | 86732 | 86732 | 29847 | USA | N45 | 1524 | ABB INC | 27511 | Supplementary Item - Extended Warranty | 2 Year Extended Warranty w/1 PM QTY (6) 1200A STS Units | PUR | 2 Year Extended Warranty w/1 PM QTY (16) 1200A STS Units | EA | EA |  | TRUE |  | P | B/W | 100 |  | 077402-12-1
133775 | 1 | 1 | States | Champlin | Hayley Fabian | TRUE | 2026-06-01T00:00:00 | 2026-10-01T00:00:00 | 2026-09-24T00:00:00 | 3 | 0 | 3 | 211.65 | 634.95 | 55316-3157 | USA | N45 | 1524 | ABB INC | 27511 | 129A501G01 | ABB TEST SWITCH 10 POLE, TEST CIRCUIT ALL BLACK HANDLES, BLACK COVER, SCREW TERMINALS | SRPP | ABB TEST SWITCH 10 POLE, TEST CIRCUIT ALL BLACK HANDLES, BLACK COVER, SCREW TERMINALS | EA | EA |  | TRUE |  | P | B/W | 100
132508 | 2 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-04-15T00:00:00 |  |  | 20000 | 17257 | 2743 | 0.3 | 12000 | 55316-3157 | USA | N30 | 1547 | SOLON MANUFACTURING COMPANY | 44194-4419 | 8L109301 | 301 1/2" Washer : ID=0.523, OD=1.063, THK=0.114, OAH=0.140 | SHMA | 301 1/2" Washer : ID=0.523, OD=1.063, THK=0.114, OAH=0.140 | EA | EA |  | TRUE |  | P | FXG | 100
132508 | 1 | 2 | States | Champlin | Robert Boulka | TRUE | 2026-04-15T00:00:00 |  |  | 30000 | 32743 | -2743 | 0.45 | 27000 | 55316-3157 | USA | N30 | 1547 | SOLON MANUFACTURING COMPANY | 44194-4419 | 616109301 | 301 3/8" Washer : ID=0.386, OD=1, THK=0.109, OAH=0.132 | SHMA | 301 3/8" Washer : ID=0.386, OD=1, THK=0.109, OAH=0.132 | EA | EA |  | TRUE |  | P | FXG
134192 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-17T00:00:00 | 2026-10-20T00:00:00 | 2026-10-20T00:00:00 | 3000 | 0 | 3000 | 2.27 | 6810 | 55316-3157 | USA | N30 | 1549 | SIERRA PACIFIC ENGINEERING AND PRODUCTS | 91189-2056 | SMCO-H-IS-01 | DOOR HINGE ASSEMBLY, 316 STAINLESS STEEL, 3.75"H, 1.3"W, .94"D | HIN | Stock Inset Door Hinge Sierra Pacific PN's:J3090 CUSTOMIZED - QTY 1J3091 CUSTOMIZED - QTY 1J3092 - QTY 1 | EA | EA |  | TRUE |  | M | FXG | 100
133225 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-05-12T00:00:00 | 2026-09-17T00:00:00 | 2026-09-17T00:00:00 | 2808 | 0 | 2808 | 2.3 | 6458.4 | 55369-6417 | USA | N30 | 1549 | SIERRA PACIFIC ENGINEERING AND PRODUCTS | 91189-2056 | SMCO-H-IS-01 | DOOR HINGE ASSEMBLY, 316 STAINLESS STEEL, 3.75"H, 1.3"W, .94"D | HIN | Stock Inset Door Hinge Sierra Pacific PN's:J3090 CUSTOMIZED - QTY 1J3091 CUSTOMIZED - QTY 1J3092 - QTY 1 | EA | EA |  | TRUE |  | M | FXG | DAYTON
132472 | 1 | 5 | States | Champlin | Megan Swymeler | TRUE | 2026-04-14T00:00:00 | 2026-11-05T00:00:00 | 2026-11-05T00:00:00 | 500 | 0 | 500 | 6.93 | 17325 | 55316-3157 | USA | N30 | 1549 | SIERRA PACIFIC ENGINEERING AND PRODUCTS | 91189-2056 | LJ123040LS | SS LOOSE JOINT HINGE, .120 THK, 3.00 OPEN x 4.00 LONG, .250 PIN, LEFT MALE & FEMALE | MEC | SS LOOSE JOINT HINGE, .120 THK, 3.00 OPEN x 4.00 LONG, .250 PIN, LEFT MALE & FEMALE | EA | EA |  | TRUE |  | P | FXG | 100
132472 | 1 | 6 | States | Champlin | Megan Swymeler | TRUE | 2026-04-14T00:00:00 | 2026-12-17T00:00:00 | 2026-12-17T00:00:00 | 500 | 0 | 500 | 6.93 | 17325 | 55316-3157 | USA | N30 | 1549 | SIERRA PACIFIC ENGINEERING AND PRODUCTS | 91189-2056 | LJ123040LS | SS LOOSE JOINT HINGE, .120 THK, 3.00 OPEN x 4.00 LONG, .250 PIN, LEFT MALE & FEMALE | MEC | SS LOOSE JOINT HINGE, .120 THK, 3.00 OPEN x 4.00 LONG, .250 PIN, LEFT MALE & FEMALE | EA | EA |  | TRUE |  | P | FXG | 100
135360 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-11T00:00:00 | 2026-11-09T00:00:00 | 2026-08-19T00:00:00 | 1500 | 0 | 1500 | 2.27 | 3405 | 55316-3157 | USA | N30 | 1549 | SIERRA PACIFIC ENGINEERING AND PRODUCTS | 91189-2056 | EML2-HINGE | STEEL, ZINC PLATED ENCLOSURE HINGE, 2.75 LONG, BOX LEAF FORMED W/3 .313 DIA HOLES, LID LEAF .281 DIA HOLE, REMOVABLE .25" DIA PIN W/FLATTENED END (ABB-1558 INVENTORY) | PUR | STEEL, ZINC PLATED ENCLOSURE HINGE, 2.75 LONG, BOX LEAF FORMED W/3 .313 DIA HOLES, LID LEAF .281 DIA HOLE, REMOVABLE .25" DIA PIN W/FLATTENED END (ABB-1558 INVENTORY) | EA | EA |  | TRUE |  | P | FXG | 100
135832 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-09-01T00:00:00 | 2026-10-07T00:00:00 | 2026-10-07T00:00:00 | 200 | 0 | 200 | 4.4 | 880 | 55369 | USA | N30 | 1549 | SIERRA PACIFIC ENGINEERING AND PRODUCTS | 91189-2056 | 41-09BK | 1/4 TURN LATCH WITH CAM | PUR | 1/4 TURN LATCH WITH CAM | EA | EA |  | TRUE |  | P | FXG | DAYTON | 2026-10-07T00:00:00
135705 | 1 | 1 | States | Dayton | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-09-01T00:00:00 |  | 15 | 0 | 15 | 0 | 0 | 55369 | USA | N30 | 1598 | MEISTER INTERNATIONAL LLC | 45241 | A20-6 | 38kV Porcelin Insulator - Indoor Bus Support | PUR | 38kV Porcelin Insulator - Indoor Bus Support | EA | EA |  | FALSE |  | P | FXG | DAYTON
132368 | 1 | 1 | States | Dayton | Holly Davis | TRUE | 2026-04-09T00:00:00 | 2026-04-14T00:00:00 | 2026-04-14T00:00:00 | 60 | 60 | 0 | 30.89 | 1853.4 | 55369-6417 | USA | N30 | 1598 | MEISTER INTERNATIONAL LLC | 45241 | 2781 | Cycloaliphatic Bus Bar Support, for 3/8" x 4" Bus Bar | PUR | Cycloaliphatic Bus Bar Support, for 3/8" x 4" Bus Bar | EA | EA |  | TRUE |  | P | B/W | DAYTON
135943 | 1 | 1 | States | Dayton | Holly Davis | TRUE | 2026-09-08T00:00:00 | 2026-10-30T00:00:00 | 2026-10-30T00:00:00 | 15 | 0 | 15 | 186.36 | 2795.4 | 55369 | USA | N30 | 1598 | MEISTER INTERNATIONAL LLC | 45241 | A30-6 | 38kV Porcelin Insulator - Indoor Bus Support | PUR | 38kV Porcelin Insulator - Indoor Bus Support | EA | EA |  | TRUE |  | P | FXG | DAYTON | 2026-09-15T00:00:00
134790 | 2 | 1 | States | Dayton | Holly Davis | TRUE | 2026-07-15T00:00:00 | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 | 255 | 0 | 255 | 34.48 | 8792.4 | 55369-6417 | USA | N30 | 1598 | MEISTER INTERNATIONAL LLC | 45241 | MI-0720310-IC | 38kV cycloaliphatic bus bar support insulators-feed through | PUR | 38kV cycloaliphatic bus bar support insulators-feed through | EA | EA |  | FALSE |  | P | FXG | DAYTON
132588 | 1 | 14 | States | Dayton | Robert Boulka | TRUE | 2026-04-17T00:00:00 |  |  | 5 | 3 | 2 | 8219 | 575330 | 55369-6417 | USA | N30 | 1619 | INDEPENDENT PACKING SERVICES INC | 55427-2786 | IPSI Quote 29562 | Material for packing unit. Includes 1 Roll PRSV033, 1/2 Roll PRSV049 & 8 Rolls Rollhstos + Labor to pack unit. | PUR | Material for packing unit. Includes 1 Roll PRSV033, 1/2 Roll PRSV049 & 8 Rolls Rollhstos + Labor to pack unit. | EA | EA |  | TRUE |  | P | W/C | DAYTON |  | 077308-4-14
134104 | 1 | 1 | States | Champlin | Taylor Barrett | TRUE | 2026-06-15T00:00:00 | 2026-12-22T00:00:00 | 2026-12-22T00:00:00 | 1 | 0 | 1 | 7358.94 | 7358.94 | 55316-3157 | USA | N30 | 1699 | COOPER POWER SYSTEMS LLC | 60673-1290 | M3RA2SR3 | 1 - Eaton / Cooper Power Systems VERTICAL GOAB Switch 35kV, 200kV BIL # M3RA2SR3 PER QUOTE GOAB PRICING LINE ITEM #6 1 - Eaton / Cooper Power Systems VERTICAL GOAB Switch 35kV, 200kV BIL # M3RA2SR3 PER QUOTE GOAB PRICING LINE ITEM #6 | Buy | "Category: --- MV - Other --- Identifier: --- 35kV Eaton GOAB - Enclosure Rating: --- Nema 3R --- - System voltage: --- 35kV --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | 100
130905 | 1 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-01-26T00:00:00 | 2026-10-19T00:00:00 | 2026-09-14T00:00:00 | 1 | 0 | 1 | 5929.5 | 5929.5 | 55369 | USA | N30 | 1699 | COOPER POWER SYSTEMS LLC | 60673-1290 | M1RA2SR2 | EATON COOOPER POWER SYSTEMS VERTICAL M FORCE GOAB QUOTE W22371635P | Buy | "Category: --- Medium Voltage --- Identifier: --- 15KV Eaton Goab ( 12 -Week Lead time) ---------------------------------- - Enclosure Rating: --- Nema 3R --- - System voltage: --- 15kV --- - Bus amperage: --- - Short Circuit Rating: --- - Applicable Listing: " | EA | EA |  | TRUE |  | P | ALL
130904 | 1 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-01-26T00:00:00 | 2026-10-19T00:00:00 |  | 1 | 0 | 1 | 7358.94 | 7358.94 | 55369 | USA | N30 | 1699 | COOPER POWER SYSTEMS LLC | 60673-1290 | M3RA2SR3 | 1 - Eaton / Cooper Power Systems VERTICAL GOAB Switch 35kV, 200kV BIL # M3RA2SR3 PER QUOTE GOAB PRICING LINE ITEM #6 1 - Eaton / Cooper Power Systems VERTICAL GOAB Switch 35kV, 200kV BIL # M3RA2SR3 PER QUOTE GOAB PRICING LINE ITEM #6 | Buy | "Category: --- MV - Other --- Identifier: --- 34.5 kV Eaton GOAB - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | ALL
135855 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-09-02T00:00:00 | 2027-05-18T00:00:00 |  | 52 | 0 | 52 | 173600 | 9027200 | 55369 | USA | D99 | 1712 | IC - VANTRAN TRANSFORMERS | 76712 | 3600kVA PMT Radial Feed | 3600kVA Padmount Transformer, Three Phase • Winding Material: Aluminum • Efficiency: Standard • High Voltage (HV): 34500 • Low Voltage (LV): 415Y/240V • Standard: IEEE/ANSI • Application: Step-Down • Sound Level: NEMA TR1 • Frequency: 60Hz • Fluid: Natural Ester • Impedance Z: 8.0% Minimum • Feed: Radial • Cooling Class: KNAN • Temp Rise: 55 Degree C • HV Tap: ±2 x 2.5% ANBN HV • 150kV BIL | PUR | 3600kVA Padmount Transformer, Three Phase • Winding Material: Aluminum • Efficiency: Standard • High Voltage (HV): 34500 • Low Voltage (LV): 415Y/240V • Standard: IEEE/ANSI • Application: Step-Down • Sound Level: NEMA TR1 • Frequency: 60Hz • Fluid: Natural Ester • Impedance Z: 8.0% Minimum • Feed: Radial • Cooling Class: KNAN • Temp Rise: 55 Degree C • HV Tap: ±2 x 2.5% ANBN HV • 150kV BIL | EA | EA |  | FALSE |  | P | B/W | DAYTON
135855 | 2 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-09-02T00:00:00 | 2027-05-18T00:00:00 |  | 20 | 0 | 20 | 168850 | 3377000 | 55369 | USA | D99 | 1712 | IC - VANTRAN TRANSFORMERS | 76712 | 3300kVA PMT Radial Feed | 3300kVA Padmount Transformer, Three Phase - Winding Material: Aluminum • Efficiency: Standard • High Voltage (HV): 34500 • Low Voltage (LV): 480Y/277V • Standard: IEEE/ANSI • Application: Step-Down • Sound Level: NEMA TR1 • Frequency: 60Hz • Fluid: Natural Ester • Impedance Z: 8.0% Minimum • Feed: Radial • Cooling Class: KNAN • Temp Rise: 55 Degree C • HV Tap: ±2 x 2.5% ANBN HV • 150kV BIL | PUR | 3300kVA Padmount Transformer, Three Phase - Winding Material: Aluminum • Efficiency: Standard • High Voltage (HV): 34500 • Low Voltage (LV): 480Y/277V • Standard: IEEE/ANSI • Application: Step-Down • Sound Level: NEMA TR1 • Frequency: 60Hz • Fluid: Natural Ester • Impedance Z: 8.0% Minimum • Feed: Radial • Cooling Class: KNAN • Temp Rise: 55 Degree C • HV Tap: ±2 x 2.5% ANBN HV • 150kV BIL | EA | EA |  | FALSE |  | P | B/W | DAYTON
133544 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-01T00:00:00 | 2026-12-01T00:00:00 | 32 | 0 | 32 | 576 | 18432 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | EA | EA |  | TRUE |  | P | B/W
133544 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-01T00:00:00 | 2026-12-01T00:00:00 | 8 | 0 | 8 | 576 | 4608 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133544 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-01T00:00:00 | 2026-12-01T00:00:00 | 4 | 0 | 4 | 576 | 2304 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
135438 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-13T00:00:00 | 2027-01-08T00:00:00 | 2027-01-08T00:00:00 | 10 | 0 | 10 | 576 | 5760 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W
135438 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-13T00:00:00 | 2027-01-08T00:00:00 | 2027-01-08T00:00:00 | 2 | 0 | 2 | 576 | 1152 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W
135438 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-13T00:00:00 | 2027-01-08T00:00:00 | 2027-01-08T00:00:00 | 4 | 0 | 4 | 576 | 2304 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 120/208VAC --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W
136182 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 4 | 0 | 4 | 576 | 2304 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | 100 | 2027-04-01T00:00:00
136182 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-04-01T00:00:00 | 2027-04-01T00:00:00 | 20 | 0 | 20 | 576 | 11520 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | 100 | 2027-04-01T00:00:00
136182 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-03-25T00:00:00 | 2027-03-25T00:00:00 | 8 | 0 | 8 | 576 | 4608 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 120/208VAC --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | 100 | 2027-03-25T00:00:00
136185 | 2 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-06-01T00:00:00 | 2027-06-01T00:00:00 | 4 | 0 | 4 | 576 | 11520 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | 100 | 2027-06-01T00:00:00
136185 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-05-25T00:00:00 | 2027-05-25T00:00:00 | 8 | 0 | 8 | 576 | 4608 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | EA | EA |  | TRUE |  | P | B/W | 100 | 2027-05-25T00:00:00
136185 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-06-01T00:00:00 | 2027-06-01T00:00:00 | 16 | 0 | 16 | 576 | 11520 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | 100 | 2027-06-01T00:00:00
133605 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2027-02-01T00:00:00 | 2027-02-01T00:00:00 | 12 | 0 | 12 | 576 | 6912 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133605 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2027-02-01T00:00:00 | 2027-02-01T00:00:00 | 12 | 0 | 12 | 576 | 6912 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133605 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2027-02-01T00:00:00 | 2027-02-01T00:00:00 | 5 | 0 | 5 | 576 | 2880 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs Audible Alarm, Form C, NEMA 4 | EA | EA |  | TRUE |  | P | B/W
136184 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-04-01T00:00:00 |  | 4 | 0 | 4 | 576 | 2304 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-04-01T00:00:00
136184 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-04-01T00:00:00 |  | 16 | 0 | 16 | 576 | 9216 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-04-01T00:00:00
136184 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-03-25T00:00:00 |  | 8 | 0 | 8 | 576 | 4608 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-03-25T00:00:00
135717 | 1 | 10 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-10-01T00:00:00 |  | 3 | 0 | 3 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77309-29-1
135717 | 1 | 21 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-12-07T00:00:00 |  | 1 | 0 | 1 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77373-35-1
135717 | 1 | 2 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-09-09T00:00:00 |  | 6 | 0 | 6 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77311-26-1
135717 | 1 | 22 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-12-14T00:00:00 |  | 4 | 0 | 4 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77319-26-1
135717 | 1 | 11 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-10-14T00:00:00 |  | 3 | 0 | 3 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77313-30-1
135717 | 1 | 25 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-09-14T00:00:00 |  | 4 | 0 | 4 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77314-25-1
135717 | 1 | 6 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-09-15T00:00:00 |  | 4 | 0 | 4 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77317-25-1
135717 | 1 | 13 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-10-19T00:00:00 |  | 4 | 0 | 4 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77315-25-1
135717 | 1 | 4 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-09-11T00:00:00 |  | 3 | 0 | 3 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77311-29-1
135717 | 1 | 23 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-12-14T00:00:00 |  | 4 | 0 | 4 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77321-24-1
135717 | 1 | 24 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2027-01-06T00:00:00 |  | 6 | 0 | 6 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77312-26-1
135717 | 1 | 8 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-09-22T00:00:00 |  | 8 | 0 | 8 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77318-27-1
135717 | 1 | 5 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-09-15T00:00:00 |  | 6 | 0 | 6 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77310-26-1
135717 | 1 | 17 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-11-09T00:00:00 |  | 3 | 0 | 3 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77312-29-1
135717 | 1 | 9 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-09-23T00:00:00 |  | 8 | 0 | 8 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77316-27-1
135717 | 1 | 12 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-10-16T00:00:00 |  | 4 | 0 | 4 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77373-24-1
135717 | 1 | 16 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-11-03T00:00:00 |  | 4 | 0 | 4 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77374-26-1
135717 | 1 | 14 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-10-22T00:00:00 |  | 6 | 0 | 6 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77309-26-1
135717 | 1 | 19 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-12-01T00:00:00 |  | 1 | 0 | 1 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77321-34-1
135717 | 1 | 15 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-10-27T00:00:00 |  | 6 | 0 | 6 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77313-27-1
135717 | 1 | 18 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-11-24T00:00:00 |  | 2 | 0 | 2 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77374-29-1
135717 | 1 | 3 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-09-10T00:00:00 |  | 3 | 0 | 3 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77310-29-1
135717 | 1 | 20 | States | Champlin | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-12-03T00:00:00 |  | 2 | 0 | 2 | 3429.96 | 325846.2 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V3-D2-INP100S-20mAOS-X | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | PUR | Shark200, Power and Energy Meter, 60Hz, 5A CT, Power Quality Harmonic Supply: 90-265VAC/1001-375VDC Ethernet 100BaseT 4 Channel Analog Output (4-20mA) ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77319-29-1
135131 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-07-31T00:00:00 | 2026-11-30T00:00:00 | 2026-11-30T00:00:00 | 5 | 0 | 5 | 576 | 2880 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W
135131 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-07-31T00:00:00 | 2026-11-30T00:00:00 | 2026-11-30T00:00:00 | 12 | 0 | 12 | 576 | 6912 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 120/208VAC --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W
135131 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-07-31T00:00:00 | 2026-11-30T00:00:00 | 2026-11-30T00:00:00 | 12 | 0 | 12 | 576 | 6912 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W
134814 | 1 | 1 | States | Champlin | Holly Davis | TRUE | 2026-07-16T00:00:00 | 2026-09-15T00:00:00 |  | 1 | 0 | 1 | 0 | 0 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V1-D2-XXX | 90-265VAC 50/60HZ Supply, 60HZ Ssensor ANSI Mount | PUR | 90-265VAC 50/60HZ Supply, 60HZ Ssensor ANSI Mount | EA | EA |  | FALSE |  | P | B/W | 100 |  | 77417-1-1
133535 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-01T00:00:00 | 2026-12-01T00:00:00 | 15 | 0 | 15 | 576 | 8640 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA | EA | EA |  | TRUE |  | P | B/W
133535 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-01T00:00:00 | 2026-12-01T00:00:00 | 6 | 0 | 6 | 576 | 3456 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133535 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-01T00:00:00 | 2026-12-01T00:00:00 | 3 | 0 | 3 | 576 | 1728 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
134732 | 1 | 2 | States | Champlin | Holly Davis | TRUE | 2026-07-14T00:00:00 | 2026-10-26T00:00:00 |  | 38 | 0 | 38 | 68.28 | 4847.88 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | EI-30CT06DR | HIGH DENSITY SHORTING TERMINAL BLOCK, 6PT ASSEMBLY | PUR | HIGH DENSITY SHORTING TERMINAL BLOCK, 6PT ASSEMBLY | EA | EA |  | TRUE |  | P | B/W | 100
133534 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-11-01T00:00:00 | 2026-11-01T00:00:00 | 3 | 0 | 3 | 576 | 1728 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133534 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-11-01T00:00:00 | 2026-11-01T00:00:00 | 15 | 0 | 15 | 576 | 8640 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | EA | EA |  | TRUE |  | P | B/W
133534 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-11-01T00:00:00 | 2026-11-01T00:00:00 | 6 | 0 | 6 | 576 | 3456 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
136183 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-04-01T00:00:00 |  | 8 | 0 | 8 | 576 | 4608 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 120/208VAC --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-04-01T00:00:00
136183 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-04-01T00:00:00 |  | 32 | 0 | 32 | 576 | 18432 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-04-01T00:00:00
136183 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-03-25T00:00:00 |  | 4 | 0 | 4 | 576 | 2304 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-03-25T00:00:00
133538 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-11-01T00:00:00 | 2026-11-01T00:00:00 | 16 | 0 | 16 | 576 | 9216 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | EA | EA |  | TRUE |  | P | B/W
133538 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-11-01T00:00:00 | 2026-11-01T00:00:00 | 8 | 0 | 8 | 576 | 4608 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133538 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-11-01T00:00:00 | 2026-11-01T00:00:00 | 4 | 0 | 4 | 576 | 2304 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133604 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2027-02-01T00:00:00 | 2027-02-01T00:00:00 | 2 | 0 | 2 | 576 | 1152 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133604 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2027-02-01T00:00:00 | 2027-02-01T00:00:00 | 10 | 0 | 10 | 576 | 5760 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs Audible Alarm, Form C, NEMA 4 | EA | EA |  | TRUE |  | P | B/W
133604 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2027-02-01T00:00:00 | 2027-02-01T00:00:00 | 4 | 0 | 4 | 576 | 2304 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
136186 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-04-01T00:00:00 |  | 4 | 0 | 4 | 576 | 2304 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-04-01T00:00:00
136186 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-04-01T00:00:00 |  | 16 | 0 | 16 | 576 | 9216 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-04-01T00:00:00
136186 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-03-25T00:00:00 |  | 8 | 0 | 8 | 576 | 4608 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-03-25T00:00:00
133543 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 16 | 0 | 16 | 576 | 9216 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | EA | EA |  | TRUE |  | P | B/W
133543 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 8 | 0 | 8 | 576 | 4608 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133543 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 4 | 0 | 4 | 576 | 2304 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133603 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2026-12-01T00:00:00 | 2026-12-01T00:00:00 | 6 | 0 | 6 | 576 | 3456 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133603 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2026-12-01T00:00:00 | 2026-12-01T00:00:00 | 15 | 0 | 15 | 576 | 8640 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | EA | EA |  | TRUE |  | P | B/W
133603 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2026-12-01T00:00:00 | 2026-12-01T00:00:00 | 3 | 0 | 3 | 576 | 1728 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
135715 | 1 | 1 | States | Dayton | Holly Davis | TRUE | 2026-08-25T00:00:00 | 2026-09-23T00:00:00 |  | 1 | 0 | 1 | 1804.87 | 1804.87 | 55369 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | SHARK250-60-10-V1-D2-INP100S-X-X | Shark250 Meter Frequency: 60 Hz System Current input: 5 A Nominal CT Secondary Multifunction Meter Only, Power supply: (90-265) V AC/DC I/O Slot 1: 100BaseT Ethernet I/O Slot 2: None Mounting: ANSI Mounting | PUR | Shark250 Meter Frequency: 60 Hz System Current input: 5 A Nominal CT Secondary Multifunction Meter Only, Power supply: (90-265) V AC/DC I/O Slot 1: 100BaseT Ethernet I/O Slot 2: None Mounting: ANSI Mounting | EA | EA |  | FALSE |  | P | B/W | DAYTON
136187 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-04-01T00:00:00 |  | 4 | 0 | 4 | 576 | 2304 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-04-01T00:00:00
136187 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-03-25T00:00:00 |  | 8 | 0 | 8 | 576 | 4608 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | PUR | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-03-25T00:00:00
136187 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-17T00:00:00 | 2027-04-01T00:00:00 |  | 16 | 0 | 16 | 576 | 9216 | 55316 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | PUR | "Category: --- LV - Other --- Identifier: --- External SPD for Panels - Mounted and Wired by EC ---------------------------------- - Enclosure Rating: --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | FALSE |  | P | B/W | 100 | 2027-04-01T00:00:00
133540 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 16 | 0 | 16 | 576 | 9216 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | EA | EA |  | TRUE |  | P | B/W
133540 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 8 | 0 | 8 | 576 | 4608 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133540 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 4 | 0 | 4 | 576 | 2304 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133547 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 32 | 0 | 32 | 576 | 18432 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | EA | EA |  | TRUE |  | P | B/W
133547 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 4 | 0 | 4 | 576 | 2304 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133547 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 8 | 0 | 8 | 576 | 4608 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133531 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-11-01T00:00:00 | 2026-11-01T00:00:00 | 3 | 0 | 3 | 576 | 1728 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71277Y050AWP2L02 | 277/480 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 277/480 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
133531 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-11-01T00:00:00 | 2026-11-01T00:00:00 | 15 | 0 | 15 | 576 | 8640 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71480D050AWP2L02 | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 |  | 480 Three Phase Delta (3W + Gnd), 50kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Audible Alarm, Form C, NEMA 4 | EA | EA |  | TRUE |  | P | B/W
133531 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-11-01T00:00:00 | 2026-11-01T00:00:00 | 6 | 0 | 6 | 576 | 3456 | 55316-3157 | USA | N30 | 1721 | DATA CENTER SYSTEMS INC | 55337 | T71120Y050AWP2L02 | 120/208 Three Phase Wye (4W + Gnd), 50 kA/Mode, 100 kA/Phase, Type 2 UL1449, LEDs, Alarm, Form C, NEMA 4X |  | 120/208 Three Phase Wye (4W+G), 50kA/Mode; 100kA/Phase AccuVar, Type 1 UL1449, Each phase is monitored, and uses combined indication by a single dual-color LED, NEMA 4X Polycarbonate | EA | EA |  | TRUE |  | P | B/W
135707 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-08-25T00:00:00 | 2026-11-16T00:00:00 | 2026-11-16T00:00:00 | 200 | 0 | 200 | 10.87 | 2174 | 55369 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-05 BK | 5 FT Cat6 Shielded Patch Cable - Black | PUR | 5 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | Dayton | 2026-09-25T00:00:00
136070 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-21T00:00:00 | 2026-09-21T00:00:00 | 100 | 0 | 100 | 18.94 | 1894 | 55316 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-15 BK | 15 FT Cat6 Shielded Patch Cable - Black | PUR | 15 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100
133883 | 3 | 1 | States | States Manufacturing Corp. | Andrew Olson | TRUE | 2026-06-04T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 100 | 0 | 100 | 23.74 | 2374 | 55316 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-25 BK | 25 FT Cat6 Shielded Patch Cable - Black | PUR | 25 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100
132891 | 7 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-04-30T00:00:00 | 2026-09-15T00:00:00 | 2026-09-15T00:00:00 | 12 | 0 | 12 | 51.99 | 623.88 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-50 BK | 50 FT Cat6 Shielded Patch Cable - Black | PUR | 50 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | DAYTON
136052 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 150 | 0 | 150 | 13.87 | 2080.5 | 55316 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 15-615-002 BK | Cat6 RJ45 Shielded Industrial Panel Mount Bulkhead Coupler with Dust Cap | PUR | Cat6 RJ45 Shielded Industrial Panel Mount Bulkhead Coupler with Dust Cap | EA | EA |  | TRUE |  | P | B/W | 100
135235 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-05T00:00:00 | 2026-09-02T00:00:00 | 2026-09-02T00:00:00 | 15 | 0 | 15 | 17.39 | 260.85 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-10 BK | 10 FT Cat6 Shielded Patch Cable - Black | PUR | 10 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-08-12T00:00:00
135235 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-05T00:00:00 | 2026-09-02T00:00:00 | 2026-09-02T00:00:00 | 55 | 15 | 40 | 14.13 | 777.15 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-07 BK | 7 FT Cat6 Shielded Patch Cable - Black | PUR | 7 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-08-12T00:00:00
135870 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-02T00:00:00 | 2026-10-02T00:00:00 | 2026-10-02T00:00:00 | 230 | 0 | 230 | 13.87 | 3190.1 | 55316 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 15-615-002 BK | Cat6 RJ45 Shielded Industrial Panel Mount Bulkhead Coupler with Dust Cap | PUR | Cat6 RJ45 Shielded Industrial Panel Mount Bulkhead Coupler with Dust Cap | EA | EA |  | TRUE |  | P | B/W | 100
132921 | 7 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-01T00:00:00 | 2026-09-15T00:00:00 | 2026-09-15T00:00:00 | 12 | 12 | 0 | 51.99 | 623.88 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-50 BK | 50 FT Cat6 Shielded Patch Cable - Black | PUR | 50 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | DAYTON
132674 | 8 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-04-22T00:00:00 | 2026-09-15T00:00:00 | 2026-09-15T00:00:00 | 32 | 17 | 15 | 51.99 | 4575.12 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-50 BK | 50 FT Cat6 Shielded Patch Cable - Black | PUR | 50 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100
133878 | 4 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-04T00:00:00 | 2026-09-29T00:00:00 | 2026-09-29T00:00:00 | 8 | 0 | 8 | 31.03 | 248.24 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-25 BK | 25 FT Cat6 Shielded Patch Cable - Black | PUR | 25 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | DAYTON
133878 | 5 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-04T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 2 | 0 | 2 | 68.99 | 137.98 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-75 BK | 75 FT Cat6 Shielded Patch Cable - Black | PUR | 75 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | DAYTON
134061 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-06-12T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 1200 | 700 | 500 | 13.73 | 32952 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-15 BK | 15 FT Cat6 Shielded Patch Cable - Black | PUR | 15 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100
134061 | 1 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-06-12T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 1200 | 500 | 700 | 13.73 | 32952 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-15 BK | 15 FT Cat6 Shielded Patch Cable - Black | PUR | 15 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100
134533 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-07-06T00:00:00 | 2026-09-07T00:00:00 | 2026-08-03T00:00:00 | 50 | 0 | 50 | 11.98 | 599 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-06 BK | 6 FT Cat6 Shielded Patch Cable - Black | PUR | 6 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-08-03T00:00:00
134533 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-07-06T00:00:00 | 2026-09-07T00:00:00 | 2026-08-03T00:00:00 | 250 | 0 | 250 | 17.39 | 4347.5 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-10 BK | 10 FT Cat6 Shielded Patch Cable - Black | PUR | 10 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-08-03T00:00:00
134533 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-07-06T00:00:00 | 2026-10-30T00:00:00 | 2026-10-30T00:00:00 | 110 | 0 | 110 | 23.53 | 2588.3 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-20 BK | 20 FT Cat6 Shielded Patch Cable - Black | PUR | 20 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-08-03T00:00:00
134533 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-07-06T00:00:00 | 2026-09-30T00:00:00 | 2026-08-03T00:00:00 | 110 | 0 | 110 | 7.09 | 779.9 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-03 BK | 3 FT Cat6 Shielded Patch Cable - Black | PUR | 3 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-08-03T00:00:00
136033 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-09-25T00:00:00 | 2026-09-25T00:00:00 | 250 | 0 | 250 | 12.82 | 3205 | 55316 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | ECF504-SC6 | CAT6 RJ45 COUPLER SHIELDED (8X8) PANEL MOUNT STYLE ETHERNET | PUR | CAT6 RJ45 COUPLER SHIELDED (8X8) PANEL MOUNT STYLE ETHERNET | EA | EA |  | TRUE |  | P | B/W | 100
135529 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-08-18T00:00:00 | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 | 50 | 0 | 50 | 9.39 | 469.5 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | M6-20-BK | 20ft CAT6 ETHERNET PATCH CABLES SNAGLESS BOOT- BLACK | PUR | 20ft CAT6 ETHERNET PATCH CABLES SNAGLESS BOOT- BLACK | EA | EA |  | TRUE |  | P | B/W | DAYTON | 2026-09-03T00:00:00
135612 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 160 | 0 | 160 | 17.39 | 2782.4 | 55316 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-10 BK | 10 FT Cat6 Shielded Patch Cable - Black | PUR | 10 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-09-21T00:00:00
135612 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-12-02T00:00:00 | 2026-12-02T00:00:00 | 180 | 0 | 180 | 7.09 | 1276.2 | 55316 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-03 BK | 3 FT Cat6 Shielded Patch Cable - Black | PUR | 3 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-09-21T00:00:00
134074 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-06-15T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 100 | 62 | 38 | 9.11 | 911 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-03 BK | 3 FT Cat6 Shielded Patch Cable - Black | PUR | 3 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100
132969 | 3 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-04T00:00:00 | 2026-09-29T00:00:00 | 2026-09-29T00:00:00 | 12 | 0 | 12 | 31.03 | 372.36 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-25 BK | 25 FT Cat6 Shielded Patch Cable - Black | PUR | 25 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | DAYTON
133649 | 1 | 4 | States | Champlin | Andrew Olson | TRUE | 2026-05-27T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 320 | 0 | 320 | 13.73 | 28901.65 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-15 BK | 15 FT Cat6 Shielded Patch Cable - Black | PUR | 15 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100
133649 | 1 | 6 | States | Champlin | Andrew Olson | TRUE | 2026-05-27T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 525 | 0 | 525 | 13.73 | 28901.65 | 55316-3157 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-15 BK | 15 FT Cat6 Shielded Patch Cable - Black | PUR | 15 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | 100
134311 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-23T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 250 | 0 | 250 | 18.94 | 4735 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-15 BK | 15 FT Cat6 Shielded Patch Cable - Black | PUR | 15 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | Dayton
134311 | 5 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-23T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 100 | 0 | 100 | 67.71 | 6771 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-75 BK | 75 FT Cat6 Shielded Patch Cable - Black | PUR | 75 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | DAYTON
134311 | 3 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-23T00:00:00 | 2026-10-30T00:00:00 | 2026-10-30T00:00:00 | 200 | 0 | 200 | 23.53 | 4706 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-20 BK | 20 FT Cat6 Shielded Patch Cable - Black | PUR | 20 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | Dayton | 2026-10-01T00:00:00
134311 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-23T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 250 | 0 | 250 | 17.39 | 4347.5 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-10 BK | 10 FT Cat6 Shielded Patch Cable - Black | PUR | 10 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | DAYTON
134311 | 4 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-23T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 200 | 0 | 200 | 31.03 | 6206 | 55369-6417 | USA | N30 | 1789 | INFINITE ELECTRONICS INTERNATIONAL INC | 91185-5176 | 610-25 BK | 25 FT Cat6 Shielded Patch Cable - Black | PUR | 25 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | TRUE |  | P | B/W | DAYTON
134794 | 2 | 1 | States | Dayton | Holly Davis | TRUE | 2026-07-15T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 200 | 0 | 200 | 0.73 | 146 | 55369-6417 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | W10-SIS-OR | Type SIS wire: 10 AWG, Orange | PUR | Type SIS wire: 10 AWG, Orange | FT | FT |  | TRUE |  | P | DEL | DAYTON
134794 | 3 | 1 | States | Dayton | Holly Davis | TRUE | 2026-07-15T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 200 | 0 | 200 | 0.73 | 146 | 55369-6417 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | W10-SIS-WT | Type SIS wire: 10 AWG, White | PUR | Type SIS wire: 10 AWG, White | FT | FT |  | TRUE |  | P | DEL | DAYTON
134794 | 4 | 1 | States | Dayton | Holly Davis | TRUE | 2026-07-15T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 200 | 0 | 200 | 0.73 | 146 | 55369-6417 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | W10-SIS-YL | Type SIS wire: 10 AWG, Yellow | PUR | Type SIS wire: 10 AWG, Yellow | FT | FT |  | TRUE |  | P | DEL | DAYTON
134794 | 1 | 1 | States | Dayton | Holly Davis | TRUE | 2026-07-15T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 200 | 0 | 200 | 0.73 | 146 | 55369-6417 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | W10-SIS-GN | 10 GA SIS GREEN 125°C TIN COPPER 105 STRAND 600V UL LISTED | PUR | 10 GA SIS GREEN 125°C TIN COPPER 105 STRAND 600V UL LISTED | FT | FT |  | TRUE |  | P | DEL | DAYTON
135762 | 1 | 6 | States | Dayton | Holly Davis | TRUE | 2026-08-27T00:00:00 | 2027-03-22T00:00:00 |  | 12 | 0 | 12 | 30.95 | 2042.7 | 55369 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | 610-35 BK | 35 FT Cat6 Shielded Patch Cable - Black | PUR | 35 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | FALSE |  | P | DEL | DAYTON
135762 | 1 | 5 | States | Dayton | Holly Davis | TRUE | 2026-08-27T00:00:00 | 2027-02-22T00:00:00 |  | 12 | 0 | 12 | 30.95 | 2042.7 | 55369 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | 610-35 BK | 35 FT Cat6 Shielded Patch Cable - Black | PUR | 35 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | FALSE |  | P | DEL | DAYTON
135762 | 1 | 7 | States | Dayton | Holly Davis | TRUE | 2026-08-27T00:00:00 | 2027-04-26T00:00:00 |  | 6 | 0 | 6 | 30.95 | 2042.7 | 55369 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | 610-35 BK | 35 FT Cat6 Shielded Patch Cable - Black | PUR | 35 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | FALSE |  | P | DEL | DAYTON
135762 | 1 | 4 | States | Dayton | Holly Davis | TRUE | 2026-08-27T00:00:00 | 2027-01-19T00:00:00 |  | 12 | 0 | 12 | 30.95 | 2042.7 | 55369 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | 610-35 BK | 35 FT Cat6 Shielded Patch Cable - Black | PUR | 35 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | FALSE |  | P | DEL | DAYTON
135762 | 1 | 1 | States | Dayton | Holly Davis | TRUE | 2026-08-27T00:00:00 | 2026-09-30T00:00:00 |  | 1 | 0 | 1 | 30.95 | 2042.7 | 55369 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | 610-35 BK | 35 FT Cat6 Shielded Patch Cable - Black | PUR | 35 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | FALSE |  | P | DEL | DAYTON
135762 | 1 | 3 | States | Dayton | Holly Davis | TRUE | 2026-08-27T00:00:00 | 2026-12-17T00:00:00 |  | 12 | 0 | 12 | 30.95 | 2042.7 | 55369 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | 610-35 BK | 35 FT Cat6 Shielded Patch Cable - Black | PUR | 35 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | FALSE |  | P | DEL | DAYTON
135762 | 1 | 2 | States | Dayton | Holly Davis | TRUE | 2026-08-27T00:00:00 | 2026-11-20T00:00:00 |  | 11 | 0 | 11 | 30.95 | 2042.7 | 55369 | USA | N30 | 1799 | STERLING WIRE AND CABLE | 55411 | 610-35 BK | 35 FT Cat6 Shielded Patch Cable - Black | PUR | 35 FT Cat6 Shielded Patch Cable - Black | EA | EA |  | FALSE |  | P | DEL | DAYTON
131538 | 2 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-03-02T00:00:00 | 2026-08-21T00:00:00 | 2026-08-15T00:00:00 | 1 | 0 | 1 | 3300 | 3300 | 55316-3157 | USA | N30 | 1802 | ASCO POWER TECHNOLOGIES LP | 55344 | D03ATSB20200FGXC | "Asco D03ATSB20070FGXC with accessory part number 948551 & 935148 1.D = Open Transition 2.03ATS = Automatic 3.B = Switched Neutral 4.2 = 2 phase poles 5.0200 = 200 amps 6.F = 240V 7.GX = With optional accessories 8.C = Type 1 enclosure 9.72EE = Ethernet communications module with Modbus TCP 10.18RX = Relay Expansion Module" | PUR | "Asco D03ATSB20070FGXC with accessory part number 948551 & 935148 1.D = Open Transition 2.03ATS = Automatic 3.B = Switched Neutral 4.2 = 2 phase poles 5.0200 = 200 amps 6.F = 240V 7.GX = With optional accessories 8.C = Type 1 enclosure 9.72EE = Ethernet communications module with Modbus TCP 10.18RX = Relay Expansion Module" | EA | EA |  | TRUE |  | P | B/W | 100
135577 | 1 | 1 | States | Champlin | Holly Davis | TRUE | 2026-08-19T00:00:00 | 2026-11-30T00:00:00 |  | 32 | 0 | 32 | 233.5 | 7472 | 55316-3157 | USA | N30 | 1819 | Total Plastics International | 49004 | GLS250 | RED GLASTIC .250 X 48 X 96 | ORM | RED GLASTIC .250 X 48 X 96 | SF | SH32 |  | FALSE |  | P | B/W | 100
136065 | 1 | 3 | States | Dayton | Holly Davis | TRUE | 2026-09-14T00:00:00 | 2027-02-01T00:00:00 |  | 50 | 0 | 50 | 122.91 | 29252.58 | 55369 | USA | N30 | 1819 | Total Plastics International | 49004 | GLS125 | RED GLASTIC .125 X 48 X 96 | ORM | RED GLASTIC .125 X 48 X 96 | SF | SH32 |  | FALSE |  | P | B/W | DAYTON
136065 | 1 | 1 | States | Dayton | Holly Davis | TRUE | 2026-09-14T00:00:00 | 2026-10-02T00:00:00 |  | 50 | 0 | 50 | 122.91 | 29252.58 | 55369 | USA | N30 | 1819 | Total Plastics International | 49004 | GLS125 | RED GLASTIC .125 X 48 X 96 | ORM | RED GLASTIC .125 X 48 X 96 | SF | SH32 |  | FALSE |  | P | B/W | DAYTON
136065 | 1 | 2 | States | Dayton | Holly Davis | TRUE | 2026-09-14T00:00:00 | 2026-12-28T00:00:00 |  | 138 | 0 | 138 | 122.91 | 29252.58 | 55369 | USA | N30 | 1819 | Total Plastics International | 49004 | GLS125 | RED GLASTIC .125 X 48 X 96 | ORM | RED GLASTIC .125 X 48 X 96 | SF | SH32 |  | FALSE |  | P | B/W | DAYTON
133126 | 1 | 1 | States | Champlin | Holly Davis | TRUE | 2026-05-08T00:00:00 | 2026-07-03T00:00:00 | 2026-05-22T00:00:00 | 200 | 88 | 112 | 112.41 | 22482 | 55316-3157 | USA | N30 | 1819 | Total Plastics International | 49004 | GLS125 | RED GLASTIC .125 X 48 X 96 | ORM | RED GLASTIC .125 X 48 X 96 | SF | SH32 |  | TRUE |  | P | B/W | 100
131676 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-03-10T00:00:00 | 2026-12-15T00:00:00 | 2026-12-15T00:00:00 | 4 | 0 | 4 | 115760 | 463040 | 55369-6417 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | Description2000kVA - 13200GrdY/7620 - 480GrdY/277 IDDes Moine Typethree phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standardANSI, IEEE, DOE, UL, NEMA Quantity4 Rated Power (kVA)2000kVA LocationOutdoor Ambient Temperature (°C)-25°C ~ +40°C Altitude(ft)3300ft Cooling systemKNAN Winding ConductorCu Phase 3 Number of Winding 2 Frequency (Hz)60 Temperature Rise (Deg C / K)65C Type of oilFR3 Primary ConnectionWye Primary Voltage Un (V)13200Y/7620 Primary Taps2 +/- 2.5 Primary Insulation (AC /BIL) (kV)95 Secondary Voltage Un (V)480Y/277 Secondary ConnectionWye Secondary Insulation (AC /BIL) (kV)30 Impedance 5.75% Efficiency Value / Standard @ 50% Load, 75deg CIEEE No-load loss/W1790 Load loss at XX°C/W (At Rating Tap)14100 ConstructionHV&LV padmounted Construction MaterialMild Steel Enclosure classificationTransformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides. Accessories1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device Factory Acceptance Tests"1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | EA | EA |  | TRUE |  | P | B/W | Dayton
136151 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-09-16T00:00:00 | 2027-08-25T00:00:00 |  | 6 | 0 | 6 | 120760 | 724560 | 55369 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 1 Rated Power (kVA): 2000kVA Location: Outdoor Ambient Temperature (°C): -25°C ~ +40°C Altitude (ft): 3300ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y/7200 Primary Taps: 2 +/- 2.5 Primary Insulation (AC /BIL) (kV): 95 Secondary Voltage Un (V): 480Y/277 Secondary Connection: Wye Secondary Insulation (AC /BIL) (kV): 30 Impedance: 5.75% Efficiency Value / Standard @ 50% Load, 75°C: IEEE No-load loss (W): 1790 Load loss at XX°C/W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." | EA | EA |  | FALSE |  | P | B/W | Dayton
136057 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-09-14T00:00:00 | 2027-05-25T00:00:00 |  | 4 | 0 | 4 | 120760 | 483040 | 55316 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | EA | EA |  | FALSE |  | P | B/W | 100
134562 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-07-13T00:00:00 | 2027-02-26T00:00:00 | 2027-02-26T00:00:00 | 4 | 0 | 4 | 117680 | 470720 | 55369-6417 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | "Category: --- MV - Other --- Identifier: --- 2000kVA - 12470GrdY/7200 - 480GrdY/277 ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | FALSE |  | P | B/W | Dayton
131681 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-03-10T00:00:00 | 2026-12-22T00:00:00 | 2026-12-22T00:00:00 | 6 | 0 | 6 | 115760 | 694560 | 55369-6417 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | "Category: --- MV - Other --- Identifier: --- 2000kVA - 12470GrdY/7200 - 480GrdY/277 ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | Dayton
131684 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-03-10T00:00:00 | 2026-12-09T00:00:00 | 2026-12-09T00:00:00 | 8 | 0 | 8 | 115760 | 926080 | 55369-6417 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | Description2000kVA - 12470D - 480GrdY/277 IDTemple Typethree phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standardANSI, IEEE, DOE, UL, NEMA Quantity8 Rated Power (kVA)2000kVA LocationOutdoor Ambient Temperature (°C)-25°C ~ +40°C Altitude(ft)3300ft Cooling systemKNAN Winding ConductorCu Phase 3 Number of Winding 2 Frequency (Hz)60 Temperature Rise (Deg C / K)65C Type of oilFR3 Primary ConnectionDelta Primary Voltage Un (V)12470 Primary Taps2 +/- 2.5 Primary Insulation (AC /BIL) (kV)95 Secondary Voltage Un (V)480Y/277 Secondary ConnectionWye Secondary Insulation (AC /BIL) (kV)30 Impedance 5.75% Efficiency Value / Standard @ 50% Load, 75deg CIEEE No-load loss/W1790 Load loss at XX°C/W (At Rating Tap)14100 ConstructionHV&LV padmounted Construction MaterialMild Steel Enclosure classificationTransformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides. | EA | EA |  | TRUE |  | P | B/W | Dayton
134563 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-07-13T00:00:00 | 2027-02-26T00:00:00 | 2027-02-26T00:00:00 | 4 | 0 | 4 | 117680 | 470720 | 55369-6417 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | "Category: --- MV - Other --- Identifier: --- 2000kVA - 12470GrdY/7200 - 480GrdY/277 ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | Dayton
136059 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-09-14T00:00:00 | 2027-03-25T00:00:00 |  | 8 | 0 | 8 | 120760 | 966080 | 55369 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | EA | EA |  | FALSE |  | P | B/W | Dayton
131682 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-03-10T00:00:00 | 2026-12-09T00:00:00 | 2026-12-09T00:00:00 | 6 | 0 | 6 | 115760 | 694560 | 55369-6417 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | "Category: --- MV - Other --- Identifier: --- 2000kVA - 12470GrdY/7200 - 480GrdY/277 ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | Dayton
131683 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-03-10T00:00:00 | 2026-12-22T00:00:00 |  | 4 | 0 | 4 | 115760 | 463040 | 55369-6417 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | "Category: --- MV - Other --- Identifier: --- 2000kVA - 12470GrdY/7200 - 480GrdY/277 ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | 100
131685 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-03-10T00:00:00 | 2026-12-09T00:00:00 | 2026-12-09T00:00:00 | 4 | 0 | 4 | 115760 | 463040 | 55369-6417 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | "Category: --- MV - Other --- Identifier: --- 2000kVA - 12470GrdY/7200 - 480GrdY/277 ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | Dayton
131686 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-03-10T00:00:00 | 2026-12-09T00:00:00 | 2026-12-09T00:00:00 | 8 | 0 | 8 | 115760 | 926080 | 55369-6417 | USA | N30 | 1825 | JST POWER EQUIPMENT, INC. | 32746 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 | 2000kVA - 12470GrdY/7200 - 480GrdY/277 "Type: three phase padmount type; oil filled; dead front, loop feed, Munsell Green, K-4 factor Reference standard: ANSI, IEEE, DOE, UL, NEMA Quantity: 2 Rated Power (kVA): 2000 kVA Location: Outdoor Ambient Temperature (°C): ?25 °C ~ +40 °C Altitude (ft): 3300 ft Cooling system: KNAN Winding Conductor: Cu Phase: 3 Number of Winding: 2 Frequency (Hz): 60 Temperature Rise (Deg C / K): 65 °C Type of oil: FR3 Primary Connection: Wye Primary Voltage Un (V): 12470Y / 7200 Primary Taps: 2 ± 2.5 Primary Insulation (AC / BIL) (kV): 95 Secondary Voltage Un (V): 480Y / 277 Secondary Connection: Wye Secondary Insulation (AC / BIL) (kV): 30 Impedance: 5.75 % Efficiency Value / Standard @ 50 % Load, 75 °C: IEEE No-load loss (W): 1790 Load loss at XX °C / W (At Rating Tap): 14100 Construction: HV & LV padmounted Construction Material: Mild Steel Enclosure classification: Transformer shall be capable of carrying loads within limits established in accordance with ANSI, C57 and NEMA loading guides." "1) Lifting lug 2) Hinged door 3) Parking stand bracket 4) LV bushings with NEMA spade terminals 5) Pressure relief valve 6) Drain valve with sampler 7) Ground strap copper 8) HV bushing wells and inserts (200A) 9) Tank grounding pads 10) Oil fill valve 11) Nameplate 12) Tap changer 13) Oil thermometer gauge 14) Oil level gauge 15) Pressure/vac gauge 16) 2-position LBOR switch 17) Bayonet + CLF 18) Surge arresters 19) Kirk key interlock for door 20) Nitrogen valve 21) Pressure relief device" "1) Routine tests. •Resistance measurements Polarity and phase-relation tests Ratio tests No-load losses and excitation current Load losses and impedance voltage Applied voltage test Induced voltage test Low-frequency test Insulation resistance test Oil sampling " | PUR | "Category: --- MV - Other --- Identifier: --- 2000kVA - 12470GrdY/7200 - 480GrdY/277 ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | B/W | 100
130372 | 2 | 6 | States | Champlin | Robert Boulka | TRUE | 2025-12-15T00:00:00 | 2027-11-03T00:00:00 | 2026-11-03T00:00:00 | 10000 | 0 | 10000 | 0.42 | 25200 | 55316 | USA | N30 | 1850 | American Belleville | 44077 | 8L109301 | 301 1/2" Washer : ID=0.523, OD=1.063, THK=0.114, OAH=0.140 | SHMA | 301 1/2" Washer : ID=0.523, OD=1.063, THK=0.114, OAH=0.140 | EA | EA |  | TRUE |  | P | FXG | 100
130372 | 1 | 6 | States | Champlin | Robert Boulka | TRUE | 2025-12-15T00:00:00 | 2026-11-03T00:00:00 | 2026-11-03T00:00:00 | 10000 | 0 | 10000 | 0.48 | 28800 | 55316 | USA | N30 | 1850 | American Belleville | 44077 | 616109301 | 301 3/8" Washer : ID=0.386, OD=1, THK=0.109, OAH=0.132 | SHMA | 301 3/8" Washer : ID=0.386, OD=1, THK=0.109, OAH=0.132 | EA | EA |  | TRUE |  | P | FXG
133734 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-29T00:00:00 | 2026-10-02T00:00:00 | 2026-10-02T00:00:00 | 14 | 0 | 14 | 398 | 5572 | 55316-3157 | USA | D01 | 1858 | MEASURLOGIC INC | 80112 | FPA-W44-1997 | Modbus gateway RS-485 to Ethernet / WiFi | PUR | Modbus gateway RS-485 to Ethernet / WiFi | EA | EA |  | TRUE |  | P | B/W | 100
132636 | 1 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-04-21T00:00:00 | 2026-10-21T00:00:00 | 2026-10-21T00:00:00 | 6 | 0 | 6 | 398 | 5174 | 55316-3157 | USA | D01 | 1858 | MEASURLOGIC INC | 80112 | FPA-W44-1997 | Modbus gateway RS-485 to Ethernet / WiFi | PUR | Modbus gateway RS-485 to Ethernet / WiFi | EA | EA |  | TRUE |  | P | B/W | 100
133258 | 1 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-05-13T00:00:00 | 2026-10-21T00:00:00 | 2026-10-21T00:00:00 | 18 | 0 | 18 | 398 | 11144 | 55316-3157 | USA | D01 | 1858 | MEASURLOGIC INC | 80112 | FPA-W44-1997 | Modbus gateway RS-485 to Ethernet / WiFi | PUR | Modbus gateway RS-485 to Ethernet / WiFi | EA | EA |  | TRUE |  | P | B/W | 100
133497 | 1 | 4 | States | Champlin | Andrew Olson | TRUE | 2026-05-21T00:00:00 | 2026-11-20T00:00:00 | 2026-11-20T00:00:00 | 16 | 0 | 16 | 398 | 39004 | 55316-3157 | USA | D01 | 1858 | MEASURLOGIC INC | 80112 | FPA-W44-1997 | Modbus gateway RS-485 to Ethernet / WiFi | PUR | Modbus gateway RS-485 to Ethernet / WiFi | EA | EA |  | TRUE |  | P | B/W | 100
133497 | 1 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-05-21T00:00:00 | 2026-10-21T00:00:00 | 2026-10-21T00:00:00 | 18 | 0 | 18 | 398 | 39004 | 55316-3157 | USA | D01 | 1858 | MEASURLOGIC INC | 80112 | FPA-W44-1997 | Modbus gateway RS-485 to Ethernet / WiFi | PUR | Modbus gateway RS-485 to Ethernet / WiFi | EA | EA |  | TRUE |  | P | B/W | 100
133497 | 1 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-05-21T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 12 | 0 | 12 | 398 | 39004 | 55316-3157 | USA | D01 | 1858 | MEASURLOGIC INC | 80112 | FPA-W44-1997 | Modbus gateway RS-485 to Ethernet / WiFi | PUR | Modbus gateway RS-485 to Ethernet / WiFi | EA | EA |  | TRUE |  | P | B/W | 100
134313 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-06-23T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 24 | 0 | 24 | 419 | 10056 | 55316-3157 | USA | D01 | 1858 | MEASURLOGIC INC | 80112 | FPA-W44-1997 | Modbus gateway RS-485 to Ethernet / WiFi | PUR | Modbus gateway RS-485 to Ethernet / WiFi | EA | EA |  | TRUE |  | P | B/W | 100
135546 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-18T00:00:00 | 2026-12-04T00:00:00 | 2026-12-04T00:00:00 | 12 | 0 | 12 | 419 | 5028 | 55316-3157 | USA | D01 | 1858 | MEASURLOGIC INC | 80112 | FPA-W44-1997 | Modbus gateway RS-485 to Ethernet / WiFi | PUR | Modbus gateway RS-485 to Ethernet / WiFi | EA | EA |  | TRUE |  | P | B/W | 100
132402 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-04-10T00:00:00 | 2026-09-15T00:00:00 | 2026-11-13T00:00:00 | 240 | 0 | 240 | 56.1 | 13464 | 55369-6417 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-035-0485-BSG-105 | 10.5" Insulator | PUR | 10.5" Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON | 2026-11-13T00:00:00
136116 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-11-04T00:00:00 | 2026-11-04T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 11 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-12-02T00:00:00 | 2026-12-02T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-11-06T00:00:00 | 2026-11-06T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 14 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-12-10T00:00:00 | 2026-12-10T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 15 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-12-14T00:00:00 | 2026-12-14T00:00:00 | 58 | 0 | 58 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 6 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-11-18T00:00:00 | 2026-11-18T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-11-10T00:00:00 | 2026-11-10T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 9 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-11-26T00:00:00 | 2026-11-26T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 13 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-12-08T00:00:00 | 2026-12-08T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 8 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-11-24T00:00:00 | 2026-11-24T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 10 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-11-30T00:00:00 | 2026-11-30T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 5 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-11-16T00:00:00 | 2026-11-16T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 12 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-12-04T00:00:00 | 2026-12-04T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 4 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-11-12T00:00:00 | 2026-11-12T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136116 | 1 | 7 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-11-20T00:00:00 | 2026-11-20T00:00:00 | 189 | 0 | 189 | 34.51 | 93315.04 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
133717 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-29T00:00:00 | 2026-11-20T00:00:00 | 2026-11-20T00:00:00 | 605 | 0 | 605 | 56.1 | 206279.7 | 55369-6417 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-035-0485-BSG-105 | 10.5" Insulator | PUR | 10.5" Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
133717 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-05-29T00:00:00 | 2026-12-23T00:00:00 | 2026-12-23T00:00:00 | 3072 | 0 | 3072 | 56.1 | 206279.7 | 55369-6417 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-035-0485-BSG-105 | 10.5" Insulator | PUR | 10.5" Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
135536 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-18T00:00:00 | 2026-10-14T00:00:00 | 2026-10-14T00:00:00 | 400 | 0 | 400 | 29.68 | 11872 | 55316-3157 | USA | N30 | 1894 | Accretion Power LLC | 15090 | INS-MV-G-6 | 6" Epoxy Insulator | PUR | 6" Epoxy Insulator | EA | EA |  | TRUE |  | P | B/W | 100
130714 | 8 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-01-14T00:00:00 | 2026-11-06T00:00:00 | 2026-11-06T00:00:00 | 306 | 0 | 306 | 29.68 | 9082.08 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | INS-MV-G-6 | 6" Epoxy Insulator | PUR | 6" Epoxy Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
134468 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-07-01T00:00:00 | 2026-10-05T00:00:00 | 2026-09-04T00:00:00 | 100 | 0 | 100 | 18.5 | 1850 | 55316-3157 | USA | N30 | 1894 | Accretion Power LLC | 15090 | INS-MV-G-3.5 | 3.5" Height (4" Dia) 3/8-16(4X) & 1/2-13 UNC(1X), 5kV 60kV - RED GLASTIC INSULATOR | INS | 3.5" Height (4" Dia) 3/8-16(4X) & 1/2-13 UNC(1X), 5kV 60kV - RED GLASTIC INSULATOR | EA | EA |  | TRUE |  | P | B/W | 100
135918 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-09-04T00:00:00 | 2027-02-15T00:00:00 | 2027-02-15T00:00:00 | 520 | 0 | 520 | 34.51 | 26917.8 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | INS-MV-G-7.5 | 7.5" Height (3.5" Dia) 3/8-16(4X) & 1/2-13 UNC(1X), 15kV 95kV - RED GLASTIC INSULATOR | INS | 7.5" Height (3.5" Dia) 3/8-16(4X) & 1/2-13 UNC(1X), 15kV 95kV - RED GLASTIC INSULATOR | EA | EA |  | TRUE |  | P | B/W | DAYTON
135918 | 1 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-09-04T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 208 | 0 | 208 | 34.51 | 26917.8 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | INS-MV-G-7.5 | 7.5" Height (3.5" Dia) 3/8-16(4X) & 1/2-13 UNC(1X), 15kV 95kV - RED GLASTIC INSULATOR | INS | 7.5" Height (3.5" Dia) 3/8-16(4X) & 1/2-13 UNC(1X), 15kV 95kV - RED GLASTIC INSULATOR | EA | EA |  | TRUE |  | P | B/W | DAYTON
136046 | 1 | 8 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-27T00:00:00 | 2026-10-27T00:00:00 | 189 | 0 | 189 | 34.51 | 61013.68 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136046 | 1 | 10 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 189 | 0 | 189 | 34.51 | 61013.68 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136046 | 1 | 4 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-13T00:00:00 | 2026-10-13T00:00:00 | 189 | 0 | 189 | 34.51 | 61013.68 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136046 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 189 | 0 | 189 | 34.51 | 61013.68 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136046 | 1 | 9 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-29T00:00:00 | 2026-10-29T00:00:00 | 189 | 0 | 189 | 34.51 | 61013.68 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136046 | 1 | 5 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 189 | 0 | 189 | 34.51 | 61013.68 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136046 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-09-18T00:00:00 | 2026-09-21T00:00:00 | 67 | 0 | 67 | 34.51 | 61013.68 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136046 | 1 | 7 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-23T00:00:00 | 2026-10-23T00:00:00 | 189 | 0 | 189 | 34.51 | 61013.68 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136046 | 1 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-07T00:00:00 | 2026-10-07T00:00:00 | 189 | 0 | 189 | 34.51 | 61013.68 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
136046 | 1 | 6 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-21T00:00:00 | 2026-10-21T00:00:00 | 189 | 0 | 189 | 34.51 | 61013.68 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-020-0311-BSG-105 | A20 20kV Standoff Insulator | PUR | A20 20kV Standoff Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
133917 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-08T00:00:00 | 2026-10-09T00:00:00 | 2026-11-20T00:00:00 | 540 | 0 | 540 | 77.81 | 42017.4 | 55369-6417 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-016-0152-BNG-000 | 5/8" x 6" Thru Bushing | PUR | 5/8" x 6" Thru Bushing | EA | EA |  | TRUE |  | P | B/W | DAYTON | 2026-11-20T00:00:00
133917 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-08T00:00:00 | 2026-10-09T00:00:00 | 2026-11-20T00:00:00 | 180 | 0 | 180 | 37.43 | 6737.4 | 55369-6417 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-006-0051-BNG-000 | 1/4" x 2" Thru Bushing | PUR | 1/4" x 2" Thru Bushing | EA | EA |  | TRUE |  | P | B/W | DAYTON | 2026-11-20T00:00:00
134076 | 4 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-15T00:00:00 | 2027-01-04T00:00:00 | 2027-01-04T00:00:00 | 384 | 0 | 384 | 56.1 | 21542.4 | 55369-6417 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-035-0485-BSG-105 | 10.5" Insulator | PUR | 10.5" Insulator | EA | EA |  | TRUE |  | P | B/W | DAYTON
134076 | 3 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-15T00:00:00 | 2027-01-04T00:00:00 | 2027-01-04T00:00:00 | 471 | 0 | 471 | 56.1 | 26423.1 | 55369-6417 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-035-0485 | 38 kV insulators- accretion power | PUR | 38 kV insulators- accretion power | EA | EA |  | TRUE |  | P | B/W | DAYTON
134076 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-15T00:00:00 | 2027-01-04T00:00:00 | 2027-01-04T00:00:00 | 150 | 0 | 150 | 37.43 | 5614.5 | 55369-6417 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-006-0051-BNG-000 | 1/4" x 2" Thru Bushing | PUR | 1/4" x 2" Thru Bushing | EA | EA |  | TRUE |  | P | B/W | DAYTON
134076 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-15T00:00:00 | 2027-01-04T00:00:00 | 2027-01-04T00:00:00 | 450 | 0 | 450 | 77.81 | 35014.5 | 55369-6417 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-016-0152-BNG-000 | 5/8" x 6" Thru Bushing | PUR | 5/8" x 6" Thru Bushing | EA | EA |  | TRUE |  | P | B/W | DAYTON
136213 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-18T00:00:00 | 2027-03-01T00:00:00 |  | 546 | 0 | 546 | 56.1 | 30630.6 | 55369 | USA | N30 | 1894 | Accretion Power LLC | 15090 | N-035-0485-BSG-105 | 10.5" Insulator | PUR | 10.5" Insulator | EA | EA |  | FALSE |  | P | B/W | DAYTON | 2027-04-26T00:00:00
135741 | 2 | 1 | States | Dayton | Holly Davis | TRUE | 2026-08-26T00:00:00 | 2026-09-04T00:00:00 | 2026-09-25T00:00:00 | 1 | 0 | 1 | 22464 | 22464 | 55369 | USA | N30 | 1898 | Ensto North America Inc | 75070 | AQ-1000-BA | Low voltage arc quenching system | PUR | Low voltage arc quenching system | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-09-04T00:00:00
135741 | 1 | 1 | States | Dayton | Holly Davis | TRUE | 2026-08-26T00:00:00 | 2026-09-04T00:00:00 | 2026-09-25T00:00:00 | 1 | 0 | 1 | 725.76 | 725.76 | 55369 | USA | N30 | 1898 | Ensto North America Inc | 75070 | AQ-101LV | ARC FLASH RELAY | PUR | ARC FLASH RELAY | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-09-04T00:00:00
135741 | 3 | 1 | States | Dayton | Holly Davis | TRUE | 2026-08-26T00:00:00 | 2026-09-04T00:00:00 | 2026-09-25T00:00:00 | 6 | 0 | 6 | 95.04 | 570.24 | 55369 | USA | N30 | 1898 | Ensto North America Inc | 75070 | Aq01-C | Arc Flash Point Sensor 50000 Lux | PUR | Arc Flash Point Sensor 50000 Lux | EA | EA |  | TRUE |  | P | B/W | 100 | 2026-09-04T00:00:00
136043 | 1 | 1 | States | Dayton | Holly Davis | TRUE | 2026-09-11T00:00:00 | 2026-09-24T00:00:00 |  | 1 | 0 | 1 | 2337.98 | 2337.98 | 55369 | USA | N30 | 1898 | Ensto North America Inc | 75070 | AQ-110PLV-AABA | "ARC FLASH RELAY 92-265 AC/VDC, T3:NO, 24VDC input." | PUR | "ARC FLASH RELAY 92-265 AC/VDC, T3:NO, 24VDC input." | EA | EA |  | FALSE |  | P | B/W | DAYTON
133588 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2026-12-14T00:00:00 | 2026-12-14T00:00:00 | 3 | 0 | 3 | 49011.6666 | 147035 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133588 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2026-12-14T00:00:00 | 2026-12-14T00:00:00 | 3 | 0 | 3 | 15748 | 47244 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133542 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-05T00:00:00 | 2026-10-05T00:00:00 | 4 | 0 | 4 | 11846 | 47384 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | 100
133542 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 4 | 0 | 4 | 76557 | 306228 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | 100
133532 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-19T00:00:00 | 2026-12-19T00:00:00 | 3 | 0 | 3 | 156480 | 469440 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | RMS Energy Co, LLC is providing a proposal for the execution of manufacturer NETA testing for States at their facility in Champlin, MN. "02PDU-AB.1 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs 02PDU-AA.1 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs 02PDU-AB.2 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs 02PDU-AA.2 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs 02PDU-BB.1 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs" "02PDU-BA.1 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs" "02UPS-A-DIST • Seven (7) LV Breakers • Four (4) Sets of CTs 02UPS-B-DIST • Seven (7) LV Breakers • Four (4) Sets of CTs 02MBP-A • Two (2) LV Breakers • One (1) Meter • One (1) Set of CTs 02MBP-B • Two (2) LV Breakers • One (1) Meter • One (1) Set of CTs 02MSB-N-1 • Seven (7) LV Breakers • One (1) Meter • One (1) Sets of CTs • Two (2) Sets of PTs 02MSB-N-2 • Twelve (12) LV Breakers • One (1) Meter • One (1) Sets of CTs • Two (2) Sets of PTs" | EA | EA |  | TRUE |  | P | PPD | 100
133532 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-14T00:00:00 | 2026-12-14T00:00:00 | 3 | 0 | 3 | 15915 | 47745 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "• Provide a short circuit, coordination, and arc flash analysis at the Chicago facility down to the 480V and 208V MCCs, Power Panels, Disconnects, and Control Panels as shown in the document listed above. o Development of an accurate update of the System Model for the facility ▪ Model to be based on an update to a customer provided native model, data contained in a previous report, and documentation provided. o Short Circuit Current Calculations and Analysis o Time Current Curve Development and Coordination Analysis o Device Duty Analysis o Arc Flash Incident Energy Analysis ▪ Calculations shall be completed in accordance with the latest version of NFPA 70E and IEEE 1584. ▪ Labels compliant with the latest version of NFPA 70E will be provided and installed for all equipment where the calculated Arc Flash Hazard exceeds 1.2cal/cm2 o An electronic report with equipment data, short circuit values, device duty analysis results, time current curves, and incident energy calculations will be provided at the completion of the analysis. o Approximately (88) Arc Flash Labels will be provided by RMS Energy and installed by Site EC. o System impedance diagrams will be printed as a PDF from the study software and presented in the final report." "States/Oppidan to provide all data and apply all labels – no site visit by RMS Energy is included in this scope of work. Data to include: • Updated available fault data from the Utility. Phase 1 values will be used unless otherwise directed by States/Oppidan. • Nameplate or drawings/datasheets for all equipment to be modeled. • As installed cable sizes and approximate lengths." "General Comments/Clarifications: • Phase 1 system model file must be provided in order to complete the above scope of work. If model files are not provided additional charges will occur and will be discussed with States/Oppidan. • The analysis will not include the following: o Equipment fed from 240V/208V transformers rated below 45KVA. o MCC loads that are below 50HP and/or 100A. o Single phase equipment. o DC equipment. • Where native software files are required in this proposal, it is assumed that a fully functional software model will be provided. If not fully functional than additional costs may apply. Examples of the files expected shall include: o Full project folder including .PRJ file for SKM o .OTI and .MDF files for ETAP o .DEZ file for EasyPower o Where custom libraries are created, they must be transmitted with the model. • Where onsite data collection is to be completed by RMS Energy under this scope, RMS will provide (1) Field Technician/Engineer to complete data collection. Customer to provide (1) NFPA 70E Trained and Qualified person to assist with locating equipment, opening doors, and removing covers as necessary to support the data collector. o While generally data can be collected safely with equipment energized, at times this cannot be safely completed without de-energizing equipment. It will be the discretion of the data collection team to determine if safety concerns exists and request equipment to be de-energized if necessary. Additional time necessary to establish safe working conditions is not included in this proposal." "• While this scope will recommend settings for devices with adjustable setpoints, the actual modification, change, or testing to the field device is not included at this time. • The equipment listed in the Project Scope Summary is RMS Energy’s best interpretation of the site equipment based on available information. • The analysis scope includes only equipment as listed in Project Scope Summary. • System model will be based on the best interpretation of the system connection based on the information that is available at the time of the quote. • Short Circuit and Device Duty Analysis will be completed based on identified equipment ratings, where equipment ratings cannot be identified they will be identified accordingly." "• The major scope of this analysis is to provide Arc Flash Hazard Analysis and labeling as part of compliance with NFPA 70E Standards for Electrical Safety in the Workplace. A detailed review of any parts of the system according to specific Health Care standards such as NFPA 70 (NEC) Article 517, NFPA 99, or others is not included in this scope. • RMS assumes that any deviation from the referenced scope of work will be billed on a T&M basis per the current RMS Energy standard rate sheet. • Services to be performed pursuant to terms and conditions agreed upon by both parties or https://www.rmsenergy.com/termsconditions • RMS requires an executed purchase order or written notice to proceed prior to commencement of work. • Any applicable taxes are not included in our price. • If within (24) hours of scheduled work, the project is cancelled, RMS will bill for travel and per diems. This includes weather delays. • Materials purchased and Travel if necessary for data collection by RMS Energy will be performed on a T&M basis and material will be invoiced at a 20% markup." | EA | EA |  | TRUE |  | P | PPD | 100
136028 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-03-25T00:00:00 |  | 4 | 0 | 4 | 156480 | 625920 | 55369 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | """Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0""" | EA | EA |  | FALSE |  | P | PPD | Dayton
136028 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-03-25T00:00:00 |  | 4 | 0 | 4 | 15915 | 63660 | 55369 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | """Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0""" | EA | EA |  | FALSE |  | P | PPD | Dayton
135130 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-07-31T00:00:00 | 2026-11-19T00:00:00 | 2026-11-19T00:00:00 | 1 | 0 | 1 | 147035 | 147035 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
135130 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-07-31T00:00:00 | 2026-11-19T00:00:00 | 2026-11-19T00:00:00 | 1 | 0 | 1 | 47244 | 47244 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
136025 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-03-25T00:00:00 |  | 4 | 0 | 4 | 15915 | 63660 | 55369 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | FALSE |  | P | PPD | Dayton
136025 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-03-25T00:00:00 |  | 4 | 0 | 4 | 156480 | 625920 | 55369 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | FALSE |  | P | PPD | Dayton
135433 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-08-13T00:00:00 | 2027-01-01T00:00:00 | 2027-01-01T00:00:00 | 2 | 0 | 2 | 156480 | 312960 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
135433 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-08-13T00:00:00 | 2027-01-01T00:00:00 | 2027-01-01T00:00:00 | 2 | 0 | 2 | 15915 | 31830 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133529 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 3 | 0 | 3 | 15915 | 47745 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133529 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 3 | 0 | 3 | 156480 | 469440 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | NETA Testing Services | EA | EA |  | TRUE |  | P | PPD | Dayton
133545 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-17T00:00:00 | 2026-12-17T00:00:00 | 4 | 0 | 4 | 11846 | 47384 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133545 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-17T00:00:00 | 2026-12-17T00:00:00 | 4 | 0 | 4 | 76557 | 306228 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133622 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-27T00:00:00 | 2027-02-08T00:00:00 | 2027-02-08T00:00:00 | 1 | 0 | 1 | 147035 | 147035 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133622 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-27T00:00:00 | 2027-02-08T00:00:00 | 2027-02-08T00:00:00 | 1 | 0 | 1 | 47244 | 47244 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
136023 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-03-25T00:00:00 |  | 4 | 0 | 4 | 15915 | 63660 | 55316 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | FALSE |  | P | PPD | 100
136023 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-04-01T00:00:00 |  | 4 | 0 | 4 | 156480 | 625920 | 55316 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | FALSE |  | P | PPD | 100
136022 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-04-01T00:00:00 |  | 4 | 0 | 4 | 156480 | 625920 | 55316 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | FALSE |  | P | PPD | 100
136022 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-03-25T00:00:00 |  | 4 | 0 | 4 | 15915 | 63660 | 55316 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | FALSE |  | P | PPD | 100
133537 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-17T00:00:00 | 2026-12-17T00:00:00 | 4 | 0 | 4 | 11846 | 47384 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133537 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-17T00:00:00 | 2026-12-17T00:00:00 | 4 | 0 | 4 | 76557 | 306228 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133541 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 4 | 0 | 4 | 76557 | 306228 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | 100
133541 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-05T00:00:00 | 2026-10-05T00:00:00 | 4 | 0 | 4 | 11846 | 47384 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | 100
133520 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-05T00:00:00 | 2026-10-05T00:00:00 | 4 | 3.2 | 0.8 | 12781 | 51124 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Provide a short circuit, coordination, and arc flash analysis at the Des Moines facility down to the 480V and 208V MCCs, Power Panels, Disconnects, and Control Panels as shown in the document listed above. o Development of an accurate update of the System Model for the facility ▪ Model to be based on an update to a customer provided native model, data contained in a previous report, and documentation provided. o Short Circuit Current Calculations and Analysis o Time Current Curve Development and Coordination Analysis o Device Duty Analysis o Arc Flash Incident Energy Analysis ▪ Calculations shall be completed in accordance with the latest version of NFPA 70E and IEEE 1584. ▪ Labels compliant with the latest version of NFPA 70E will be provided and installed for all equipment where the calculated Arc Flash Hazard exceeds 1.2cal/cm2 o An electronic report with equipment data, short circuit values, device duty analysis results, time current curves, and incident energy calculations will be provided at the completion of the analysis. o Approximately (58) Arc Flash Labels will be provided by RMS Energy and installed by Site EC. o System impedance diagrams will be printed as a PDF from the study software and presented in the final report." "States/Oppidan to provide all data and apply all labels – no site visit by RMS Energy is included in this scope of work. Data to include: • Updated available fault data from the Utility. Phase 1 values will be used unless otherwise directed by States/Oppidan. • Nameplate or drawings/datasheets for all equipment to be modeled. • As installed cable sizes and approximate lengths." "General Comments/Clarifications: • Phase 1 system model file must be provided in order to complete the above scope of work. If model files are not provided additional charges will occur and will be discussed with States/Oppidan. • The analysis will not include the following: o Equipment fed from 240V/208V transformers rated below 45KVA. o MCC loads that are below 50HP and/or 100A. o Single phase equipment. o DC equipment. • Where native software files are required in this proposal, it is assumed that a fully functional software model will be provided. If not fully functional than additional costs may apply. Examples of the files expected shall include: o Full project folder including .PRJ file for SKM o .OTI and .MDF files for ETAP o .DEZ file for EasyPower o Where custom libraries are created, they must be transmitted with the model." "• Where onsite data collection is to be completed by RMS Energy under this scope, RMS will provide (1) Field Technician/Engineer to complete data collection. Customer to provide (1) NFPA 70E Trained and Qualified person to assist with locating equipment, opening doors, and removing covers as necessary to support the data collector. o While generally data can be collected safely with equipment energized, at times this cannot be safely completed without de-energizing equipment. It will be the discretion of the data collection team to determine if safety concerns exists and request equipment to be de-energized if necessary. Additional time necessary to establish safe working conditions is not included in this proposal. • While this scope will recommend settings for devices with adjustable setpoints, the actual modification, change, or testing to the field device is not included at this time. • The equipment listed in the Project Scope Summary is RMS Energy’s best interpretation of the site equipment based on available information. • The analysis scope includes only equipment as listed in Project Scope Summary. • System model will be based on the best interpretation of the system connection based on the information that is available at the time of the quote. • Short Circuit and Device Duty Analysis will be completed based on identified equipment ratings, where equipment ratings cannot be identified they will be identified accordingly." "• The major scope of this analysis is to provide Arc Flash Hazard Analysis and labeling as part of compliance with NFPA 70E Standards for Electrical Safety in the Workplace. A detailed review of any parts of the system according to specific Health Care standards such as NFPA 70 (NEC) Article 517, NFPA 99, or others is not included in this scope. • RMS assumes that any deviation from the referenced scope of work will be billed on a T&M basis per the current RMS Energy standard rate sheet. • Services to be performed pursuant to terms and conditions agreed upon by both parties or https://www.rmsenergy.com/termsconditions • RMS requires an executed purchase order or written notice to proceed prior to commencement of work. • Any applicable taxes are not included in our price. • If within (24) hours of scheduled work, the project is cancelled, RMS will bill for travel and per diems. This includes weather delays. • Materials purchased and Travel if necessary for data collection by RMS Energy will be performed on a T&M basis and material will be invoiced at a 20% markup." | EA | EA |  | TRUE |  | P | PPD | 100
133520 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 4 | 0 | 4 | 76557 | 306228 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | RMS Energy Co, LLC is providing a proposal for the execution of manufacturer NETA testing for States at their facility in Champlin, MN. "02PDU-AB.1 • Twelve (12) LV Breakers • One (1) Meters • One (1) Set of CTs" "02PDU-AA.1 • Twelve (12) LV Breakers • One (1) Meters • One (1) Sets of CTs" "02PDU-AB.2 • Twelve (12) LV Breakers • One (1) Meters • One (1) Sets of CTs" "02PDU-AA.2 • Twelve (12) LV Breakers • One (1) Meters • One (1) Sets of CTs" "02UPS-A-DIST • Fourteen (14) LV Breakers • Four (4) Meters • Four (4) Sets of CTs" "02MBP-A • Two (2) LV Breakers • One (1) Meter • One (1) Set of CTs" "02MSB-N-1 • Eleven (11) LV Breakers • Three (3) Meters • Three (3) Sets of CTs • Two (2) Sets of PTs" | EA | EA |  | TRUE |  | P | PPD | 100
133536 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2027-02-08T00:00:00 | 2027-02-08T00:00:00 | 3 | 0 | 3 | 156480 | 469440 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133536 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2027-02-08T00:00:00 | 2027-02-08T00:00:00 | 3 | 0 | 3 | 15915 | 47745 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133546 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2027-01-04T00:00:00 | 2027-01-04T00:00:00 | 4 | 0 | 4 | 76557 | 306228 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | 100
133546 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-28T00:00:00 | 2026-12-28T00:00:00 | 4 | 0 | 4 | 11846 | 47384 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | 100
133533 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-21T00:00:00 | 2026-12-21T00:00:00 | 3 | 0 | 3 | 156480 | 469440 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | RMS Energy Co, LLC is providing a proposal for the execution of manufacturer NETA testing for States at their facility in Champlin, MN. "02PDU-AB.1 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs" "02PDU-AA.1 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs" "02PDU-AB.2 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs" "02PDU-AA.2 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs" "02PDU-BB.1 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs" "02PDU-BA.1 • Twelve (12) LV Breakers • Twelve (12) Meters • Twelve (12) Sets of CTs" "02UPS-A-DIST • Seven (7) LV Breakers • Four (4) Sets of CTs" "02UPS-B-DIST • Seven (7) LV Breakers • Four (4) Sets of CTs" "02MBP-A • Two (2) LV Breakers • One (1) Meter • One (1) Set of CTs" "02MBP-B • Two (2) LV Breakers • One (1) Meter • One (1) Set of CTs" "02MSB-N-1 • Seven (7) LV Breakers • One (1) Meter • One (1) Sets of CTs • Two (2) Set | EA | EA |  | TRUE |  | P | PPD | 100
133533 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-22T00:00:00 | 2026-12-07T00:00:00 | 2026-12-07T00:00:00 | 3 | 0 | 3 | 15915 | 47745 | 55316-3157 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | 100
133591 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2027-02-08T00:00:00 | 2027-02-08T00:00:00 | 2 | 0 | 2 | 13949 | 27898 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
133591 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-05-26T00:00:00 | 2027-02-08T00:00:00 | 2027-02-08T00:00:00 | 2 | 0 | 2 | 129162 | 258324 | 55369-6417 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | "Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0" | EA | EA |  | TRUE |  | P | PPD | Dayton
136020 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-06-01T00:00:00 |  | 4 | 0 | 4 | 156480 | 625920 | 55316 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | FALSE |  | P | PPD | 100
136020 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-05-25T00:00:00 |  | 4 | 0 | 4 | 15915 | 63660 | 55316 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | FALSE |  | P | PPD | 100
136024 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-03-25T00:00:00 |  | 4 | 0 | 4 | 156480 | 625920 | 55369 | USA | N30 | 1953 | RMS ENERGY | 56345 | NETA Testing Services | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | Category: --- LV - Other --- Identifier: --- NETA Testing Services ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | FALSE |  | P | PPD | Dayton
136024 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2027-03-25T00:00:00 |  | 4 | 0 | 4 | 15915 | 63660 | 55369 | USA | N30 | 1953 | RMS ENERGY | 56345 | Short Circuit, Coordination, and Arc Flash Study A | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | Buy | Category: --- LV - Other --- Identifier: --- Short Circuit, Coordination, and Arc Flash Study Analysis ---------------------------------- - Enclosure Rating: --- - System voltage: --- - Bus amperage: --- - Short Circuit Rating: --- - Sections: --- 0 | EA | EA |  | FALSE |  | P | PPD | Dayton
133825 | 5 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-03T00:00:00 | 2026-10-16T00:00:00 | 2026-10-16T00:00:00 | 6 | 0 | 6 | 1356 | 8136 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0323/400K/RJ/H | 9567/0323/400K/RJ/H, 15” tail 150kV BiL, 3300:1 ratio with 400K ohm load, 30’ casted-in RJ45 cable (For 5 SEL-751 (2M/5 = 400K ohm) Capable of Hi-pot @50kv for 1 minute | PUR | 9567/0323/400K/RJ/H, 15” tail 150kV BiL, 3300:1 ratio with 400K ohm load, 30’ casted-in RJ45 cable (For 5 SEL-751 (2M/5 = 400K ohm) Capable of Hi-pot @50kv for 1 minute | EA | EA |  | TRUE |  | P | PPD | DAYTON
133825 | 4 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-03T00:00:00 | 2026-10-16T00:00:00 | 2026-10-16T00:00:00 | 12 | 0 | 12 | 1356 | 16272 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0323/333K/RJ/H | 9567/0323/333K/RJ/H, 15” tail 1590V BiL, 3300:1 ratio with 333K ohm load, 30’ casted-in RJ45 cable (For 6 SEL-751 (2M ohm/6 = 333k ohm)) Capable of Hi-pot @50kv for 1 minute | PUR | 9567/0323/333K/RJ/H, 15” tail 1590V BiL, 3300:1 ratio with 333K ohm load, 30’ casted-in RJ45 cable (For 6 SEL-751 (2M ohm/6 = 333k ohm)) Capable of Hi-pot @50kv for 1 minute | EA | EA |  | TRUE |  | P | PPD | DAYTON
133825 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-03T00:00:00 | 2026-10-16T00:00:00 | 2026-10-16T00:00:00 | 24 | 0 | 24 | 1356 | 32544 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0323/286K/RJ/H | 9567/0323/286K/RJ/H, 15” tail 150kV BiL, 3300:1 ratio with 286Kohm load, 30’ casted-in RJ45 cable (For 7 SEL-751 (2M ohm/7 = 286K ohm) Capable of Hi-pot @50kv for 1 minute | PUR | 9567/0323/286K/RJ/H, 15” tail 150kV BiL, 3300:1 ratio with 286Kohm load, 30’ casted-in RJ45 cable (For 7 SEL-751 (2M ohm/7 = 286K ohm) Capable of Hi-pot @50kv for 1 minute | EA | EA |  | TRUE |  | P | PPD | DAYTON
133825 | 7 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-03T00:00:00 | 2026-10-16T00:00:00 | 2026-10-16T00:00:00 | 42 | 0 | 42 | 500 | 21000 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 95Patch-8 | 95Patch-8, patch panel for connecting 7 SEL-751 | PUR | 95Patch-8, patch panel for connecting 7 SEL-751 | EA | EA |  | TRUE |  | P | PPD | DAYTON
133825 | 3 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-03T00:00:00 | 2026-10-16T00:00:00 | 2026-10-16T00:00:00 | 66 | 0 | 66 | 1556 | 102696 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0323/2M/RJ/H | 9567/0323/2M/RJ/H, 15” tail 150kV BiL, 3300:1 ratio with 2M ohm load, 30’ casted-in RJ45 cable (For 1 SEL-751 (2M ohm) Capable of Hi-pot @50kv for 1 minute | PUR | 9567/0323/2M/RJ/H, 15” tail 150kV BiL, 3300:1 ratio with 2M ohm load, 30’ casted-in RJ45 cable (For 1 SEL-751 (2M ohm) Capable of Hi-pot @50kv for 1 minute | EA | EA |  | TRUE |  | P | PPD | DAYTON
133825 | 2 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-03T00:00:00 | 2026-10-16T00:00:00 | 2026-10-16T00:00:00 | 14 | 0 | 14 | 1471 | 20594 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0323/2M/H | 9567/0323/2M/H, 15” tail 150kV BiL, 3300:1 ratio with 2M ohm load, 30’ casted-in pigtail (For 1 SEL-751 (SYNC check) Capable of Hi-pot @50kv for 1 minute | PUR | 9567/0323/2M/H, 15” tail 150kV BiL, 3300:1 ratio with 2M ohm load, 30’ casted-in pigtail (For 1 SEL-751 (SYNC check) Capable of Hi-pot @50kv for 1 minute | EA | EA |  | TRUE |  | P | PPD | DAYTON
133825 | 6 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-03T00:00:00 | 2026-10-16T00:00:00 | 2026-10-16T00:00:00 | 42 | 0 | 42 | 1471 | 61782 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0723/5M/H | 9567/0723/5M/H, 15” tail 150kV BiL, 166:1 ratio with 5M ohm load, 30’ casted-in pigtail (For 1 SEL-735 (5M ohm) Capable of Hi-pot @50kv for 1 minute | PUR | 9567/0723/5M/H, 15” tail 150kV BiL, 166:1 ratio with 5M ohm load, 30’ casted-in pigtail (For 1 SEL-735 (5M ohm) Capable of Hi-pot @50kv for 1 minute | EA | EA |  | TRUE |  | P | PPD | DAYTON
134246 | 3 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-22T00:00:00 | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 | 6 | 0 | 6 | 1132 | 16980 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0323/2M/H | 9567/0323/2M/H, 15” tail 150kV BiL, 3300:1 ratio with 2M ohm load, 30’ casted-in pigtail (For 1 SEL-751 (SYNC check) Capable of Hi-pot @50kv for 1 minute | PUR | 9567/0323/2M/H, 15” tail 150kV BiL, 3300:1 ratio with 2M ohm load, 30’ casted-in pigtail (For 1 SEL-751 (SYNC check) Capable of Hi-pot @50kv for 1 minute | EA | EA |  | TRUE |  | P | PPD | DAYTON
134246 | 3 | 2 | States | Dayton | Megan Swymeler | TRUE | 2026-06-22T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 6 | 0 | 6 | 1132 | 16980 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0323/2M/H | 9567/0323/2M/H, 15” tail 150kV BiL, 3300:1 ratio with 2M ohm load, 30’ casted-in pigtail (For 1 SEL-751 (SYNC check) Capable of Hi-pot @50kv for 1 minute | PUR | 9567/0323/2M/H, 15” tail 150kV BiL, 3300:1 ratio with 2M ohm load, 30’ casted-in pigtail (For 1 SEL-751 (SYNC check) Capable of Hi-pot @50kv for 1 minute | EA | EA |  | TRUE |  | P | PPD | DAYTON
134246 | 4 | 2 | States | Dayton | Megan Swymeler | TRUE | 2026-06-22T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 6 | 0 | 6 | 1457 | 17484 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0X23/285/5M/H | 9567/0X23/285/5M/H, 15” tall, 150kV BiL standoff, 285:1 ratio with 5M ohm load, 30’ pigtail cable, 50kV 1Min Hi-Pot (use for SEL-735) | PUR | 9567/0X13/285/5M/H, 15” tall, 150kV BiL standoff, 285:1 ratio with 5M ohm load, 30’ pigtail cable, 50kV 1Min Hi-Pot (use for SEL-735) | EA | EA |  | TRUE |  | P | PPD | DAYTON
134246 | 4 | 3 | States | Dayton | Megan Swymeler | TRUE | 2026-06-22T00:00:00 | 2027-01-19T00:00:00 | 2027-01-19T00:00:00 | 3 | 0 | 3 | 1457 | 17484 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0X23/285/5M/H | 9567/0X23/285/5M/H, 15” tall, 150kV BiL standoff, 285:1 ratio with 5M ohm load, 30’ pigtail cable, 50kV 1Min Hi-Pot (use for SEL-735) | PUR | 9567/0X13/285/5M/H, 15” tall, 150kV BiL standoff, 285:1 ratio with 5M ohm load, 30’ pigtail cable, 50kV 1Min Hi-Pot (use for SEL-735) | EA | EA |  | TRUE |  | P | PPD | DAYTON
134246 | 3 | 3 | States | Dayton | Megan Swymeler | TRUE | 2026-06-22T00:00:00 | 2027-01-19T00:00:00 | 2027-01-19T00:00:00 | 3 | 0 | 3 | 1132 | 16980 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0323/2M/H | 9567/0323/2M/H, 15” tail 150kV BiL, 3300:1 ratio with 2M ohm load, 30’ casted-in pigtail (For 1 SEL-751 (SYNC check) Capable of Hi-pot @50kv for 1 minute | PUR | 9567/0323/2M/H, 15” tail 150kV BiL, 3300:1 ratio with 2M ohm load, 30’ casted-in pigtail (For 1 SEL-751 (SYNC check) Capable of Hi-pot @50kv for 1 minute | EA | EA |  | TRUE |  | P | PPD | DAYTON
134246 | 4 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-22T00:00:00 | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 | 3 | 0 | 3 | 1457 | 17484 | 55369-6417 | USA | N30 | 1957 | Lindsey Systems | 91702 | 9567/0X23/285/5M/H | 9567/0X23/285/5M/H, 15” tall, 150kV BiL standoff, 285:1 ratio with 5M ohm load, 30’ pigtail cable, 50kV 1Min Hi-Pot (use for SEL-735) | PUR | 9567/0X13/285/5M/H, 15” tall, 150kV BiL standoff, 285:1 ratio with 5M ohm load, 30’ pigtail cable, 50kV 1Min Hi-Pot (use for SEL-735) | EA | EA |  | TRUE |  | P | PPD | DAYTON
135937 | 1 | 1 | States | Forgent Power Solutions | Holly Davis | TRUE | 2026-09-08T00:00:00 | 2026-09-16T00:00:00 |  | 1 | 0 | 1 | 2638 | 2638 | 55369 | USA | N30 | 1962 | HIPOTRONICS | 19605 | 100HVT-DI | AC HIPOT DIGITAL 100KV 5KVA Catalog No.: 100HVT-DI Commodity Code: 9030390100 | TOOL | HIPOT Test Fixture | EA | EA |  | FALSE |  | P | PPD
135244 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-05T00:00:00 | 2026-08-12T00:00:00 | 2026-08-12T00:00:00 | 1 | 1 | 0 | 454.98 | 454.98 | 55369-6417 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 590-500 | Current Transformer: 50:5 current ratio, C15 relay class | PUR | Current Transformer: 50:5 current ratio, C15 relay class | EA | EA |  | TRUE |  | P | PPD | DAYTON
134683 | 2 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-07-13T00:00:00 | 2026-08-12T00:00:00 | 2026-08-12T00:00:00 | 2 | 0 | 2 | 74.98 | 599.84 | 55369-6417 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5202202 | 3.5 gal Titebond Fast Grab FRP Panel Adhesive | PUR | 3.5 gal Titebond Fast Grab FRP Panel Adhesive | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
134683 | 1 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-07-13T00:00:00 | 2026-08-12T00:00:00 | 2026-08-12T00:00:00 | 8 | 0 | 8 | 7.99 | 191.76 | 55369-6417 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5090051 | 5/8" x 10' White PVC FRP Inside Corner Moulding | PUR | 5/8" x 10' White PVC FRP Inside Corner Moulding | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
134683 | 2 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-07-13T00:00:00 | 2026-08-12T00:00:00 | 2026-08-12T00:00:00 | 2 | 0 | 2 | 74.98 | 599.84 | 55369-6417 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5202202 | 3.5 gal Titebond Fast Grab FRP Panel Adhesive | PUR | 3.5 gal Titebond Fast Grab FRP Panel Adhesive | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
134683 | 2 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-07-13T00:00:00 | 2026-08-12T00:00:00 | 2026-08-12T00:00:00 | 2 | 0 | 2 | 74.98 | 599.84 | 55369-6417 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5202202 | 3.5 gal Titebond Fast Grab FRP Panel Adhesive | PUR | 3.5 gal Titebond Fast Grab FRP Panel Adhesive | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
134683 | 1 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-07-13T00:00:00 | 2026-08-12T00:00:00 | 2026-08-12T00:00:00 | 8 | 0 | 8 | 7.99 | 191.76 | 55369-6417 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5090051 | 5/8" x 10' White PVC FRP Inside Corner Moulding | PUR | 5/8" x 10' White PVC FRP Inside Corner Moulding | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
136015 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-09-11T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 8 | 0 | 8 | 7.99 | 319.6 | 55369 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5090051 | 5/8" x 10' White PVC FRP Inside Corner Moulding | PUR | 5/8" x 10' White PVC FRP Inside Corner Moulding | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
136015 | 2 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-09-11T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 1 | 0 | 1 | 39.98 | 159.92 | 55369 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5202202 | 3.5 gal Titebond Fast Grab FRP Panel Adhesive | PUR | 3.5 gal Titebond Fast Grab FRP Panel Adhesive | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
136015 | 3 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-09-11T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 1088 | 0 | 1088 | 1 | 1088 | 55369 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | PLY-.375-48X96 | CDX Plywood - 48" x 96" 3/8" | PUR | CDX Plywood - 48" x 96" 3/8" | SF | SF | Mena | TRUE |  | P | PPD | Dayton
136015 | 2 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-09-11T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 3 | 0 | 3 | 39.98 | 159.92 | 55369 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5202202 | 3.5 gal Titebond Fast Grab FRP Panel Adhesive | PUR | 3.5 gal Titebond Fast Grab FRP Panel Adhesive | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
136015 | 1 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-09-11T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 8 | 0 | 8 | 7.99 | 319.6 | 55369 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5090051 | 5/8" x 10' White PVC FRP Inside Corner Moulding | PUR | 5/8" x 10' White PVC FRP Inside Corner Moulding | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
136015 | 1 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-09-11T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 8 | 0 | 8 | 7.99 | 319.6 | 55369 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5090051 | 5/8" x 10' White PVC FRP Inside Corner Moulding | PUR | 5/8" x 10' White PVC FRP Inside Corner Moulding | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
136015 | 1 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-09-11T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 16 | 0 | 16 | 7.99 | 319.6 | 55369 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | 5090051 | 5/8" x 10' White PVC FRP Inside Corner Moulding | PUR | 5/8" x 10' White PVC FRP Inside Corner Moulding | EA | EA | Mena | TRUE |  | P | PPD | DAYTON
135252 | 1 | 1 | States | States Manufacturing Corp. | Robert Boulka | TRUE | 2026-08-05T00:00:00 | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 | 500 | 0 | 500 | 1.2604 | 630.2 | 55316 | USA | D99 | 1970 | RAMP BUSINESS CORPORATION | 10010 | N1500040 | 300MCM (40mm Pin) Non Insulated Ferrules (25 pieces) | SUP | 300MCM Non Insulated Wire Ferrules | EA | EA |  | TRUE |  | P | PPD
134283 | 1 | 1 | States | Champlin | Hayley Fabian | TRUE | 2026-06-22T00:00:00 | 2026-11-18T00:00:00 | 2026-09-30T00:00:00 | 4 | 0 | 4 | 4053.4 | 16213.6 | 55316-3157 | USA | N30 | 2002 | DEHN INC | 28115 | ISM2504003YF | 250kA per mode, 500kA per phase, 230/400C, 3Ph wye, 4 wire+ groud, filter | PUR | 250kA per mode, 500kA per phase, 230/400C, 3Ph wye, 4 wire+ groud, filter | EA | EA |  | TRUE |  | P | PPD | 100
134312 | 2 | 1 | States | Champlin | Hayley Fabian | TRUE | 2026-06-23T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 1 | 0 | 1 | 1671.15 | 1671.15 | 55316-3157 | USA | N30 | 2002 | DEHN INC | 28115 | CGP31004803YPLF-T2 | -100kA per mode, 200kA per phase -277/480v, 3-phase Wye, 4 wire + ground -Polycarbonate with | PUR | -100kA per mode, 200kA per phase -277/480v, 3-phase Wye, 4 wire + ground -Polycarbonate with | EA | EA |  | TRUE |  | P | PPD | 100 |  | 077178-1-1
134312 | 1 | 1 | States | Champlin | Hayley Fabian | TRUE | 2026-06-23T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 5 | 0 | 5 | 1671.15 | 8355.75 | 55316-3157 | USA | N30 | 2002 | DEHN INC | 28115 | CGP31004803DPLF-T2 | 100kA per mode, 200kA per phase -480v, 3-phaseDelta, 3 wire + ground -Polycarbonate with termination lugs -Status indicator LED lights (one per phase), dry relay contacts, audible alarm with silence button, fault light + Surge counter | PUR | 100kA per mode, 200kA per phase -480v, 3-phaseDelta, 3 wire + ground -Polycarbonate with termination lugs -Status indicator LED lights (one per phase), dry relay contacts, audible alarm with silence button, fault light + Surge counter | EA | EA |  | TRUE |  | P | PPD | 100 |  | 077178-1-1
134281 | 1 | 1 | States | Champlin | Hayley Fabian | TRUE | 2026-06-22T00:00:00 | 2026-11-18T00:00:00 | 2026-09-30T00:00:00 | 1 | 0 | 1 | 4053.4 | 4053.4 | 55316-3157 | USA | N30 | 2002 | DEHN INC | 28115 | ISM2504003YF | 250kA per mode, 500kA per phase, 230/400C, 3Ph wye, 4 wire+ groud, filter | PUR | 250kA per mode, 500kA per phase, 230/400C, 3Ph wye, 4 wire+ groud, filter | EA | EA |  | TRUE |  | P | PPD | 100
134282 | 1 | 1 | States | Champlin | Hayley Fabian | TRUE | 2026-06-22T00:00:00 | 2026-11-18T00:00:00 | 2026-09-30T00:00:00 | 2 | 0 | 2 | 4053.4 | 8106.8 | 55316-3157 | USA | N30 | 2002 | DEHN INC | 28115 | ISM2504003YF | 250kA per mode, 500kA per phase, 230/400C, 3Ph wye, 4 wire+ groud, filter | PUR | 250kA per mode, 500kA per phase, 230/400C, 3Ph wye, 4 wire+ groud, filter | EA | EA |  | TRUE |  | P | PPD | 100
133663 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2027-01-08T00:00:00 |  | 2 | 0 | 2 | 105264 | 210528 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
132811 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 1 | 0.5 | 0.5 | 346633 | 346633 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QPS-250169 | EA | EA |  | TRUE |  | P | PPD | 100
136161 | 1 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-09-16T00:00:00 | 2026-09-28T00:00:00 | 2026-09-28T00:00:00 | 1 | 0 | 1 | 57036 | 57036 | 55369 | USA | D99 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133692 | 3 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 1 | 0 | 1 | 75000 | 75000 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133692 | 2 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 1 | 0.5 | 0.5 | 311225 | 311225 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
134910 | 1 | 1 | States | Champlin | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2026-08-03T00:00:00 |  | 3 | 0 | 3 | 0 | 0 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | RD21050MBGA | INTELIVISION 1050 TOUCH, 10.1" DISPLAY UNIT | PUR | INTELIVISION 1050 TOUCH, 10.1" DISPLAY UNIT | EA | EA |  | FALSE |  | P | PPD | 100
135569 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-19T00:00:00 |  |  | 1 | 0 | 1 | 12245 | 12245 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133179 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-11T00:00:00 | 2026-11-02T00:00:00 |  | 1 | 0 | 1 | 126952 | 126952 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | DAYTON
135357 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-08-11T00:00:00 | 2026-08-21T00:00:00 | 2026-08-21T00:00:00 | 1 | 0 | 1 | 49390 | 49390 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133682 | 3 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 1 | 0 | 1 | 386225 | 386225 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133682 | 2 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 1 | 0 | 1 | 386225 | 386225 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
132875 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-04-30T00:00:00 |  |  | 1 | 0 | 1 | 346633 | 346633 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133693 | 2 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 1 | 0 | 1 | 75000 | 75000 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133693 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 1 | 0 | 1 | 311225 | 311225 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
132874 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-04-30T00:00:00 |  |  | 1 | 0 | 1 | 346633 | 346633 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
135373 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-08-11T00:00:00 | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 | 1 | 0 | 1 | 94943 | 94943 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133661 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2027-06-01T00:00:00 |  | 4 | 0 | 4 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
135662 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-08-24T00:00:00 |  |  | 1 | 0 | 1 | 25000 | 25000 | 55316 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
132871 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-04-30T00:00:00 |  |  | 1 | 0 | 1 | 346633 | 346633 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
135422 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-12T00:00:00 | 2026-08-19T00:00:00 | 2026-08-19T00:00:00 | 1 | 0 | 1 | 1750 | 1750 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133667 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 4 | 0 | 4 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133657 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2027-04-01T00:00:00 |  | 4 | 0 | 4 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133217 | 2 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-12T00:00:00 |  |  | 42 | 0 | 42 | 3090 | 129780 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133217 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-12T00:00:00 |  |  | 42 | 0 | 42 | 6180 | 259560 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133218 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-12T00:00:00 |  |  | 42 | 0 | 42 | 6180 | 259560 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133218 | 2 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-12T00:00:00 |  |  | 42 | 0 | 42 | 3090 | 129780 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133668 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 4 | 0 | 4 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
132876 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-04-30T00:00:00 |  |  | 1 | 0 | 1 | 386225 | 386225 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133670 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 4 | 2 | 2 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
132812 | 1 | 25 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 1 | 0 | 1 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 20 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 7 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 2 | 1 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 17 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 2 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 120 | 60 | 60 | 3500 | 420000 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 2 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 15 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 8 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 16 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 10 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 23 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 2 | 0 | 2 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 9 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 13 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 11 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 26 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 1 | 0 | 1 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 19 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 22 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 18 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 27 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 1 | 0 | 1 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 14 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 24 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 1 | 0 | 1 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 21 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
132812 | 1 | 12 | States | Dayton | Robert Boulka | TRUE | 2026-04-28T00:00:00 |  |  | 3 | 0 | 3 | 39600 | 2851200 | 55369-6417 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning Ref Quote QFP 302307 Line 1 | EA | EA |  | TRUE |  | P | PPD | 100
133655 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2027-04-01T00:00:00 |  | 4 | 0 | 4 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133215 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-12T00:00:00 | 2026-12-15T00:00:00 |  | 116 | 0 | 116 | 6180 | 716880 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133215 | 2 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-12T00:00:00 | 2026-12-15T00:00:00 |  | 116 | 0 | 116 | 3090 | 358440 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133680 | 2 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-11-20T00:00:00 | 2026-11-20T00:00:00 | 1 | 0 | 1 | 0 | 0 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133656 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2027-04-01T00:00:00 |  | 4 | 2 | 2 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
135812 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-31T00:00:00 | 2027-02-26T00:00:00 |  | 8 | 0 | 8 | 78000 | 624000 | 55369 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | DAYTON
133671 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 3 | 0 | 3 | 105264 | 315792 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133216 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-12T00:00:00 |  |  | 1 | 0 | 1 | 203400 | 203400 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133672 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 3 | 0 | 3 | 105264 | 315792 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133660 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2027-04-01T00:00:00 |  | 4 | 2 | 2 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133666 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 4 | 0 | 4 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
136180 | 1 | 1 | States | Champlin | Taylor Barrett | TRUE | 2026-09-17T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 1 | 0 | 1 | 50078 | 50078 | 55316 | USA | D99 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100 | 2026-10-01T00:00:00
133665 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 4 | 0 | 4 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133679 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 4 | 0 | 4 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133675 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 3 | 0 | 3 | 105264 | 315792 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133659 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2027-04-01T00:00:00 |  | 4 | 0 | 4 | 105264 | 421056 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133664 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 2 | 0 | 2 | 105264 | 210528 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
133674 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 3 | 0 | 3 | 105264 | 315792 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
132873 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-04-30T00:00:00 |  |  | 1 | 0 | 1 | 112114 | 112114 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
133677 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-05-28T00:00:00 | 2026-12-31T00:00:00 |  | 3 | 0 | 3 | 105264 | 315792 | 55316-3157 | USA | N30 | 2018 | IC - ARES ENERGY LP / PWRQ SYSTEMS | 21076 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | FALSE |  | P | PPD | 100
135578 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-19T00:00:00 | 2026-10-15T00:00:00 | 2026-10-15T00:00:00 | 7 | 0 | 7 | 877.25 | 28072 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF_EL-RHR-FR9 | 4 - 0 X 9 - 0 16GA 4 1/4" JAMB WELDED HM FRAME (REMOVABLE TRANSOM/ASTRAGAL BY OTHERS) *PRIMED* | PUR | 4 - 0 X 9 - 0 16GA 4 1/4" JAMB WELDED HM FRAME (REMOVABLE TRANSOM/ASTRAGAL BY OTHERS) *PRIMED* | EA | EA |  | TRUE |  | P | PPD | DAYTON
135578 | 1 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-08-19T00:00:00 | 2026-10-15T00:00:00 | 2026-10-15T00:00:00 | 15 | 0 | 15 | 877.25 | 28072 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF_EL-RHR-FR9 | 4 - 0 X 9 - 0 16GA 4 1/4" JAMB WELDED HM FRAME (REMOVABLE TRANSOM/ASTRAGAL BY OTHERS) *PRIMED* | PUR | 4 - 0 X 9 - 0 16GA 4 1/4" JAMB WELDED HM FRAME (REMOVABLE TRANSOM/ASTRAGAL BY OTHERS) *PRIMED* | EA | EA |  | TRUE |  | P | PPD | DAYTON
135578 | 1 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-08-19T00:00:00 | 2026-10-15T00:00:00 | 2026-10-15T00:00:00 | 10 | 0 | 10 | 877.25 | 28072 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF_EL-RHR-FR9 | 4 - 0 X 9 - 0 16GA 4 1/4" JAMB WELDED HM FRAME (REMOVABLE TRANSOM/ASTRAGAL BY OTHERS) *PRIMED* | PUR | 4 - 0 X 9 - 0 16GA 4 1/4" JAMB WELDED HM FRAME (REMOVABLE TRANSOM/ASTRAGAL BY OTHERS) *PRIMED* | EA | EA |  | TRUE |  | P | PPD | DAYTON
135742 | 1 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-08-26T00:00:00 | 2026-12-11T00:00:00 |  | 10 | 0 | 10 | 5402 | 172864 | 55369 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | HMD-EL-RHR | RHR PD DOORS/HDW ONLY (Right Hand Swing) 4 - 0 X 8 - 0 18GA INSULATED HM FLUSH DOOR *PAINTED* | PUR | RHR PD DOORS/HDW ONLY (Right Hand Swing) 4 - 0 X 8 - 0 18GA INSULATED HM FLUSH DOOR *PAINTED* | EA | EA |  | FALSE |  | P | PPD | DAYTON
135742 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-26T00:00:00 | 2026-12-11T00:00:00 |  | 7 | 0 | 7 | 5402 | 172864 | 55369 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | HMD-EL-RHR | RHR PD DOORS/HDW ONLY (Right Hand Swing) 4 - 0 X 8 - 0 18GA INSULATED HM FLUSH DOOR *PAINTED* | PUR | RHR PD DOORS/HDW ONLY (Right Hand Swing) 4 - 0 X 8 - 0 18GA INSULATED HM FLUSH DOOR *PAINTED* | EA | EA |  | FALSE |  | P | PPD | DAYTON
135742 | 1 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-08-26T00:00:00 | 2026-12-11T00:00:00 |  | 15 | 0 | 15 | 5402 | 172864 | 55369 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | HMD-EL-RHR | RHR PD DOORS/HDW ONLY (Right Hand Swing) 4 - 0 X 8 - 0 18GA INSULATED HM FLUSH DOOR *PAINTED* | PUR | RHR PD DOORS/HDW ONLY (Right Hand Swing) 4 - 0 X 8 - 0 18GA INSULATED HM FLUSH DOOR *PAINTED* | EA | EA |  | FALSE |  | P | PPD | DAYTON
134264 | 4 | 5 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-09-17T00:00:00 | 2026-09-17T00:00:00 | 10 | 0 | 10 | 5235 | 261750 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-PD | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-09-17T00:00:00
134264 | 4 | 2 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 | 8 | 0 | 8 | 5235 | 261750 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-PD | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-08-06T00:00:00
134264 | 1 | 6 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 9 | 0 | 9 | 3987 | 199350 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-10-01T00:00:00
134264 | 4 | 3 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-08-20T00:00:00 | 2026-08-20T00:00:00 | 8 | 0 | 8 | 5235 | 261750 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-PD | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-08-20T00:00:00
134264 | 1 | 2 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 | 8 | 0 | 8 | 3987 | 199350 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-08-06T00:00:00
134264 | 3 | 4 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-09-03T00:00:00 | 2026-09-03T00:00:00 | 9 | 0 | 9 | 5235 | 261750 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-PD | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-09-03T00:00:00
134264 | 3 | 2 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 | 8 | 0 | 8 | 5235 | 261750 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-PD | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-08-06T00:00:00
134264 | 1 | 5 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-09-17T00:00:00 | 2026-09-17T00:00:00 | 10 | 0 | 10 | 3987 | 199350 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-09-17T00:00:00
134264 | 2 | 2 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 | 8 | 0 | 8 | 3987 | 199350 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-MD | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-08-06T00:00:00
134264 | 1 | 3 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-08-20T00:00:00 | 2026-08-20T00:00:00 | 8 | 0 | 8 | 3987 | 199350 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-08-20T00:00:00
134264 | 3 | 6 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 9 | 0 | 9 | 5235 | 261750 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-PD | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-10-01T00:00:00
134264 | 2 | 6 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 9 | 0 | 9 | 3987 | 199350 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-MD | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-10-01T00:00:00
134264 | 2 | 5 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-09-17T00:00:00 | 2026-09-17T00:00:00 | 10 | 0 | 10 | 3987 | 199350 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-MD | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-09-17T00:00:00
134264 | 4 | 4 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-09-03T00:00:00 | 2026-09-03T00:00:00 | 9 | 0 | 9 | 5235 | 261750 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-PD | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-09-03T00:00:00
134264 | 3 | 3 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-08-20T00:00:00 | 2026-08-20T00:00:00 | 8 | 0 | 8 | 5235 | 261750 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-PD | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-08-20T00:00:00
134264 | 1 | 4 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-09-03T00:00:00 | 2026-09-03T00:00:00 | 9 | 0 | 9 | 3987 | 199350 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-09-03T00:00:00
134264 | 3 | 5 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-09-17T00:00:00 | 2026-09-17T00:00:00 | 10 | 0 | 10 | 5235 | 261750 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-PD | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-09-17T00:00:00
134264 | 4 | 6 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 9 | 0 | 9 | 5235 | 261750 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-PD | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-10-01T00:00:00
134264 | 2 | 4 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-09-03T00:00:00 | 2026-09-03T00:00:00 | 9 | 0 | 9 | 3987 | 199350 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-MD | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-09-03T00:00:00
134264 | 2 | 3 | States | TIMMERMAN FINISHING INC | Robert Boulka | TRUE | 2026-06-22T00:00:00 | 2026-08-20T00:00:00 | 2026-08-20T00:00:00 | 8 | 0 | 8 | 3987 | 199350 | 55421 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-MD | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-08-20T00:00:00
135040 | 1 | 5 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-18T00:00:00 |  | 9 | 0 | 9 | 4712 | 197904 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 4 | 5 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-18T00:00:00 |  | 9 | 0 | 9 | 5960 | 250320 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-PD | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 4 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-10-14T00:00:00 | 2026-10-14T00:00:00 | 8 | 0 | 8 | 5960 | 250320 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-PD | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 3 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-04T00:00:00 |  | 7 | 0 | 7 | 4712 | 197904 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-MD | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 3 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-10-28T00:00:00 | 2026-10-28T00:00:00 | 8 | 0 | 8 | 4712 | 197904 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-MD | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 2 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-04T00:00:00 |  | 7 | 0 | 7 | 5960 | 250320 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-PD | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 1 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-04T00:00:00 |  | 7 | 0 | 7 | 4712 | 197904 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 2 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-10-28T00:00:00 | 2026-10-28T00:00:00 | 8 | 0 | 8 | 5960 | 250320 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-PD | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 1 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-11T00:00:00 |  | 10 | 0 | 10 | 4712 | 197904 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 4 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-11T00:00:00 |  | 10 | 0 | 10 | 5960 | 250320 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-PD | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 4 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-10-28T00:00:00 | 2026-10-28T00:00:00 | 8 | 0 | 8 | 5960 | 250320 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-PD | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 1 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-10-28T00:00:00 | 2026-10-28T00:00:00 | 8 | 0 | 8 | 4712 | 197904 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 3 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-11T00:00:00 |  | 10 | 0 | 10 | 4712 | 197904 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-MD | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-10-14T00:00:00 | 2026-10-14T00:00:00 | 8 | 0 | 8 | 4712 | 197904 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 2 | 5 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-18T00:00:00 |  | 9 | 0 | 9 | 5960 | 250320 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-PD | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 2 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-10-14T00:00:00 | 2026-10-14T00:00:00 | 8 | 0 | 8 | 5960 | 250320 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-PD | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 4 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-04T00:00:00 |  | 7 | 0 | 7 | 5960 | 250320 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-PD | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 3 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-10-14T00:00:00 | 2026-10-14T00:00:00 | 8 | 0 | 8 | 4712 | 197904 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-MD | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 3 | 5 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-18T00:00:00 |  | 9 | 0 | 9 | 4712 | 197904 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-RHR-MD | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Right Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135040 | 2 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-11-11T00:00:00 |  | 10 | 0 | 10 | 5960 | 250320 | 55369-6417 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-PD | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Powered Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | TRUE |  | P | PPD | DAYTON
135778 | 1 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-08-28T00:00:00 | 2026-12-04T00:00:00 |  | 17 | 0 | 17 | 4712 | 150784 | 55369 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | FALSE |  | P | PPD | DAYTON
135778 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-28T00:00:00 | 2026-11-19T00:00:00 |  | 15 | 0 | 15 | 4712 | 150784 | 55369 | USA | N30 | 2025 | LaFORCE HOLDINGS LLC | 54303 | WHMF-V2-LHR-MD | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | PUR | 48" Manual Door (Left Hand Swing) 4 - 0 x 8 - 0 18 GA INSULATED HM FLUSH DOOR *PRIMED* + QUOTED HDW | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 3 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-03-22T00:00:00 | 2027-03-22T00:00:00 | 72 | 0 | 72 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 1 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2026-11-20T00:00:00 |  | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 1 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-04-26T00:00:00 | 2027-04-26T00:00:00 | 90 | 0 | 90 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 1 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-01-19T00:00:00 | 2027-01-19T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 3 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2026-12-17T00:00:00 |  | 72 | 0 | 72 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 1 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2026-12-17T00:00:00 |  | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 3 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2026-11-20T00:00:00 |  | 72 | 0 | 72 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 2 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-01-19T00:00:00 | 2027-01-19T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 3 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-04-26T00:00:00 | 2027-04-26T00:00:00 | 36 | 0 | 36 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 2 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2026-11-20T00:00:00 |  | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 2 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 2 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-04-26T00:00:00 | 2027-04-26T00:00:00 | 90 | 0 | 90 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 1 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-03-22T00:00:00 | 2027-03-22T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 3 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-01-19T00:00:00 | 2027-01-19T00:00:00 | 72 | 0 | 72 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 3 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 72 | 0 | 72 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 2 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2026-12-17T00:00:00 |  | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 1 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
134895 | 2 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-07-20T00:00:00 | 2027-03-22T00:00:00 | 2027-03-22T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38I1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | FALSE |  | P | PPD | DAYTON
133928 | 4 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-02-15T00:00:00 | 2027-02-15T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 5 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-01-11T00:00:00 | 2027-01-11T00:00:00 | 12 | 0 | 12 | 22566.85 | 1489412.1 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | DPE-36NF, 34500v3/115v3 0.3Y | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | PUR | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 5 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-02-15T00:00:00 | 2027-02-15T00:00:00 | 12 | 0 | 12 | 22566.85 | 1489412.1 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | DPE-36NF, 34500v3/115v3 0.3Y | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | PUR | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 5 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-05-24T00:00:00 | 2027-05-24T00:00:00 | 6 | 0 | 6 | 22566.85 | 1489412.1 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | DPE-36NF, 34500v3/115v3 0.3Y | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | PUR | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 5 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-03-16T00:00:00 | 2027-03-16T00:00:00 | 12 | 0 | 12 | 22566.85 | 1489412.1 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | DPE-36NF, 34500v3/115v3 0.3Y | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | PUR | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 7 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2026-12-08T00:00:00 | 2026-12-08T00:00:00 | 12 | 0 | 12 | 20826.82 | 1374570.12 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E20-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 1 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-03-16T00:00:00 | 2027-02-22T00:00:00 | 60 | 0 | 60 | 18863.12 | 6224829.6 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E12-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 7 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-04-13T00:00:00 | 2027-03-25T00:00:00 | 12 | 0 | 12 | 20826.82 | 1374570.12 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E20-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 2 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2026-12-08T00:00:00 | 2026-12-08T00:00:00 | 72 | 0 | 72 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 3 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-02-15T00:00:00 | 2027-02-15T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 2 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-05-24T00:00:00 | 2027-05-24T00:00:00 | 36 | 0 | 36 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 6 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-02-15T00:00:00 | 2027-01-25T00:00:00 | 60 | 0 | 60 | 16731.16 | 5521282.8 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E12-A23678S EXPS | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 3 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-04-13T00:00:00 | 2027-04-13T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 4 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-05-24T00:00:00 | 2027-05-24T00:00:00 | 90 | 0 | 90 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 1 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-02-15T00:00:00 | 2027-01-25T00:00:00 | 60 | 0 | 60 | 18863.12 | 6224829.6 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E12-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 4 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-03-16T00:00:00 | 2027-03-16T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 1 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-01-11T00:00:00 | 2026-12-21T00:00:00 | 60 | 0 | 60 | 18863.12 | 6224829.6 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E12-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 7 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-01-11T00:00:00 | 2027-01-11T00:00:00 | 12 | 0 | 12 | 20826.82 | 1374570.12 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E20-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 8 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-03-16T00:00:00 | 2027-02-22T00:00:00 | 12 | 0 | 12 | 17185.91 | 1134270.06 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E20-A23678S EXPS | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 6 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2026-12-08T00:00:00 | 2026-12-08T00:00:00 | 60 | 0 | 60 | 16731.16 | 5521282.8 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E12-A23678S EXPS | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 7 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-03-16T00:00:00 | 2027-02-22T00:00:00 | 12 | 0 | 12 | 20826.82 | 1374570.12 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E20-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 3 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-01-11T00:00:00 | 2027-01-11T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 3 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-05-24T00:00:00 | 2027-05-24T00:00:00 | 90 | 0 | 90 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 8 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2026-12-08T00:00:00 | 2026-11-20T00:00:00 | 12 | 0 | 12 | 17185.91 | 1134270.06 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E20-A23678S EXPS | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 7 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-05-24T00:00:00 | 2027-04-26T00:00:00 | 6 | 0 | 6 | 20826.82 | 1374570.12 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E20-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 7 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-02-15T00:00:00 | 2027-01-25T00:00:00 | 12 | 0 | 12 | 20826.82 | 1374570.12 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E20-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 2000A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 8 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-04-13T00:00:00 | 2027-03-25T00:00:00 | 12 | 0 | 12 | 17185.91 | 1134270.06 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E20-A23678S EXPS | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 8 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-01-11T00:00:00 | 2026-12-21T00:00:00 | 12 | 0 | 12 | 17185.91 | 1134270.06 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E20-A23678S EXPS | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 6 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-01-11T00:00:00 | 2027-01-11T00:00:00 | 60 | 0 | 60 | 16731.16 | 5521282.8 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E12-A23678S EXPS | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 1 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2026-12-08T00:00:00 | 2026-11-20T00:00:00 | 60 | 0 | 60 | 18863.12 | 6224829.6 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E12-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 6 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-04-13T00:00:00 | 2027-03-25T00:00:00 | 60 | 0 | 60 | 16731.16 | 5521282.8 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E12-A23678S EXPS | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 3 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2026-12-08T00:00:00 | 2026-12-08T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 6 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-05-24T00:00:00 | 2027-04-26T00:00:00 | 30 | 0 | 30 | 16731.16 | 5521282.8 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E12-A23678S EXPS | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 5 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-04-13T00:00:00 | 2027-04-13T00:00:00 | 12 | 0 | 12 | 22566.85 | 1489412.1 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | DPE-36NF, 34500v3/115v3 0.3Y | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | PUR | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 3 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-03-16T00:00:00 | 2027-03-16T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-103030 | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 4 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-01-11T00:00:00 | 2027-01-11T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 2 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-03-16T00:00:00 | 2027-03-16T00:00:00 | 72 | 0 | 72 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 8 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-02-15T00:00:00 | 2027-01-25T00:00:00 | 12 | 0 | 12 | 17185.91 | 1134270.06 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E20-A23678S EXPS | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 2 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-04-13T00:00:00 | 2027-04-13T00:00:00 | 72 | 0 | 72 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 2 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-02-15T00:00:00 | 2027-02-15T00:00:00 | 72 | 0 | 72 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 8 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-05-24T00:00:00 | 2027-04-26T00:00:00 | 6 | 0 | 6 | 17185.91 | 1134270.06 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E20-A23678S EXPS | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV, 2000A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 4 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-04-13T00:00:00 | 2027-04-13T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 2 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-01-11T00:00:00 | 2027-01-11T00:00:00 | 72 | 0 | 72 | 554.53 | 219593.88 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A2-103030 | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | PUR | Multi-Ration CT 2000:5A, C400, for a 2000A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 6 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-03-16T00:00:00 | 2027-02-22T00:00:00 | 60 | 0 | 60 | 16731.16 | 5521282.8 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVCH-38D32E12-A23678S EXPS | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | PUR | Cradle, 38kV,1200A, 31.5kA, Direct Roll-In Lead Wire: A2 (10a10B) Standard set (Shutter padlock, TOC,MOC): A3(4a4b(MOC,TOC)) Door: A6 Door interlock: A7 Door emergency push button: A8 Insulation Ring: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 1 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-04-13T00:00:00 | 2027-03-25T00:00:00 | 60 | 0 | 60 | 18863.12 | 6224829.6 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E12-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 1 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-05-24T00:00:00 | 2027-04-26T00:00:00 | 30 | 0 | 30 | 18863.12 | 6224829.6 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | UVH-38H32E12-M7C7T7SC4U0-A78ES EXPS | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | PUR | VCB, DO, Susol, 38kV, 1200A, 31.5kA Motor: M7 (120VAC) Closing Coil: C7 (120VAC) Shunt Trip Coil: T7 (125VAC) Auxiliary Contacts & Connector Type: SC4 (10a10b Standard Type, Auto-con Type) Under Voltage Release: U0 (Without UVT) Keylock: A7 (Keylock(Individual key)) Button Padlock: A8 (Button Padlock) MOC Operator: AE Aux Wheels: AS | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 5 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2026-12-08T00:00:00 | 2026-12-08T00:00:00 | 12 | 0 | 12 | 22566.85 | 1489412.1 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | DPE-36NF, 34500v3/115v3 0.3Y | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | PUR | PT Drawer, 36.5kV with 3-PTS-300:1, 19920:66.5V, 170kV BIL, 60Hz, 0.5E | EA | EA |  | TRUE |  | P | PPD | DAYTON
133928 | 4 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2026-12-08T00:00:00 | 2026-12-08T00:00:00 | 180 | 0 | 180 | 554.53 | 548984.7 | 55369-6417 | USA | N30 | 2030 | LS ELECTRIC AMERICA INC | 60069 | C-38A1-102020 | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | PUR | Multi-Ration CT 1200:5A, C400, for a 1200A VCB | EA | EA |  | TRUE |  | P | PPD | DAYTON
135534 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-08-18T00:00:00 | 2026-11-23T00:00:00 | 2026-11-23T00:00:00 | 172 | 0 | 172 | 68 | 11696 | 55369-6417 | USA | N30 | 2064 | CG HILL AND SONS INC | 55112 | SWG-BLD-GB-01 | GROUNDING BLOCK | PUR | SS Grounding Block 4.5" x 1" x 4.25" | EA | EA |  | TRUE |  | P | PPD | DAYTON
134867 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-07-20T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 264 | 0 | 264 | 68 | 17952 | 55369-6417 | USA | N30 | 2064 | CG HILL AND SONS INC | 55112 | SWG-BLD-GB-01 | GROUNDING BLOCK | PUR | SS Grounding Block 4.5" x 1" x 4.25" | EA | EA |  | TRUE |  | P | PPD | DAYTON
134845 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-07-17T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 4 | 0 | 4 | 68 | 272 | 55369-6417 | USA | N30 | 2064 | CG HILL AND SONS INC | 55112 | SWG-BLD-GB-01 | GROUNDING BLOCK | PUR | SS Grounding Block 4.5" x 1" x 4.25" | EA | EA |  | TRUE |  | P | PPD | DAYTON
134507 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-07-02T00:00:00 | 2026-09-01T00:00:00 | 2026-09-01T00:00:00 | 212 | 0 | 212 | 68 | 32640 | 55369-6417 | USA | N30 | 2064 | CG HILL AND SONS INC | 55112 | SWG-BLD-GB-01 | GROUNDING BLOCK | PUR | SS Grounding Block 4.5" x 1" x 4.25" | EA | EA |  | TRUE |  | P | PPD | DAYTON
135297 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-07T00:00:00 |  |  | 444 | 100 | 344 | 11 | 4884 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | MD- STOCK_DOORSTOP REV A | MARYLAND DOOR STOP | PUR | MARYLAND DOOR STOP | EA | EA |  | TRUE |  | P | PPD | DAYTON
135990 | 2 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-09-10T00:00:00 | 2027-01-08T00:00:00 |  | 1 | 0 | 1 | 11801.53 | 11801.53 | 55369 | USA | D99 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77417-2 | Category: --- LV - 891 --- Identifier: --- DP2 (MLO) ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 1 | FGS | Category: --- LV - 891 --- Identifier: --- DP2 (MLO) ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 1 | EA | EA |  | FALSE |  | M | PPD | 100
135990 | 3 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-09-10T00:00:00 | 2027-01-08T00:00:00 |  | 1 | 0 | 1 | 8884.03 | 8884.03 | 55369 | USA | D99 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77417-3 | Category: --- LV - 891 --- Identifier: --- DP1 (MLO) ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- 800A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 1 | FGS | Category: --- LV - 891 --- Identifier: --- DP1 (MLO) ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- 800A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 1 | EA | EA |  | FALSE |  | M | PPD | 100
135990 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-09-10T00:00:00 | 2027-01-08T00:00:00 |  | 1 | 0 | 1 | 63900.71 | 63900.71 | 55369 | USA | D99 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77417-1 | Category: --- LV - 891 --- Identifier: --- MCB N1 (SERVICE ENTRANCE RATED) ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 3 | FGS | Category: --- LV - 891 --- Identifier: --- MCB N1 (SERVICE ENTRANCE RATED) ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 277/480VAC (3P 4W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 3 | EA | EA |  | FALSE |  | M | PPD | 100
134463 | 2 | 6 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-09-28T00:00:00 |  | 6 | 0 | 6 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 11 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-11-02T00:00:00 |  | 8 | 0 | 8 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-09-14T00:00:00 |  | 6 | 0 | 6 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 6 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-09-28T00:00:00 |  | 6 | 0 | 6 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 9 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-10-19T00:00:00 |  | 8 | 0 | 8 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-08-24T00:00:00 |  | 4 | 0 | 4 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 11 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2027-11-02T00:00:00 |  | 8 | 0 | 8 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-08-31T00:00:00 |  | 4 | 0 | 4 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 14 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-08-17T00:00:00 |  | 1 | 0 | 1 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 10 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-10-26T00:00:00 |  | 8 | 0 | 8 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-09-07T00:00:00 |  | 4 | 0 | 4 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 13 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-08-17T00:00:00 |  | 1 | 0 | 1 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 7 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-10-05T00:00:00 |  | 6 | 0 | 6 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-08-24T00:00:00 |  | 4 | 0 | 4 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 8 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-10-12T00:00:00 |  | 6 | 0 | 6 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-09-07T00:00:00 |  | 4 | 0 | 4 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 7 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-10-05T00:00:00 |  | 6 | 0 | 6 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 8 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-10-12T00:00:00 |  | 6 | 0 | 6 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 4 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-11-09T00:00:00 |  | 4 | 0 | 4 | 254319 | 1017276 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-12B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A - CORE EPOD Only ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 0 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A - CORE EPOD Only ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 12 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-11-09T00:00:00 |  | 4 | 0 | 4 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 5 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-09-21T00:00:00 |  | 6 | 0 | 6 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 10 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-10-26T00:00:00 |  | 8 | 0 | 8 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 5 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-09-21T00:00:00 |  | 6 | 0 | 6 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-08-31T00:00:00 |  | 4 | 0 | 4 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 2 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-09-14T00:00:00 |  | 6 | 0 | 6 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1B | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 3 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-11-09T00:00:00 |  | 4 | 0 | 4 | 254319 | 1017276 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-12A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A - CORE EPOD Only ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 0 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A - CORE EPOD Only ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 12 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-11-09T00:00:00 |  | 4 | 0 | 4 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
134463 | 1 | 9 | States | Dayton | Robert Boulka | TRUE | 2026-06-30T00:00:00 | 2026-10-19T00:00:00 |  | 8 | 0 | 8 | 254319 | 18310968 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77411-1A | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | FGS | Category: --- LV - 891 --- Identifier: --- Main Switchboard MSB-1A ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 4000A --- - Short Circuit Rating: --- 65KAIC --- - Sections: --- 7 | EA | EA |  | FALSE |  | M | PPD | DAYTON
135490 | 1 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 |  | 2 | 0 | 2 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 8 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-08-28T00:00:00 |  | 2 | 0 | 2 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 |  | 2 | 0 | 2 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 |  | 2 | 0 | 2 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 10 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-09-14T00:00:00 |  | 4 | 0 | 4 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 |  | 2 | 0 | 2 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 11 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-09-21T00:00:00 |  | 4 | 0 | 4 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 9 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-09-04T00:00:00 |  | 4 | 0 | 4 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 7 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-08-21T00:00:00 |  | 2 | 0 | 2 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 12 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-09-28T00:00:00 |  | 4 | 0 | 4 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 5 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 |  | 2 | 0 | 2 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
135490 | 1 | 6 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-08-17T00:00:00 |  | 2 | 0 | 2 | 120503 | 3856096 | 55369-6417 | USA | N30 | 2072 | IC - ALLIED TRADING INC/dba PWRQ | 21076 | 77414-2 | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | FGS | Category: --- LV - 891 --- Identifier: --- Mechanical Block ---------------------------------- - Enclosure Rating: --- Nema 1 --- - System voltage: --- 480VAC (3P 3W) --- - Bus amperage: --- 1600A --- - Short Circuit Rating: --- 42KAIC --- - Sections: --- 6 | EA | EA |  | FALSE |  | P | PPD | DAYTON
133170 | 2 | 8 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-10-12T00:00:00 | 15 | 0 | 15 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 9 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-10-19T00:00:00 | 20 | 0 | 20 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 12 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-10-19T00:00:00 | 20 | 0 | 20 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 13 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-10-19T00:00:00 | 16 | 0 | 16 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-09-14T00:00:00 | 10 | 0 | 10 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-09-08T00:00:00 | 10 | 0 | 10 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-09-21T00:00:00 | 15 | 0 | 15 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 11 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-10-19T00:00:00 | 20 | 0 | 20 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 | 2026-09-08T00:00:00 | 2026-07-27T00:00:00 | 4 | 3 | 1 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-08-24T00:00:00 | 10 | 0 | 10 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 10 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-10-19T00:00:00 | 20 | 0 | 20 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 | 2026-09-11T00:00:00 | 2026-08-24T00:00:00 | 6 | 0 | 6 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
133170 | 2 | 7 | States | Dayton | Taylor Barrett | TRUE | 2026-05-11T00:00:00 |  | 2026-09-21T00:00:00 | 15 | 0 | 15 | 118000 | 21358000 | 55369-6417 | USA | N30 | 2090 | DAEDEX / MAS HVAC | 55369 | ECTPUA060A4654ERVPCS | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | PUR | Outdoor packaged DX e-house cooling unit, consisting of (2) redundant, fully independent 30-ton Air Cooled Condensing Units, Air Handling Units with Centrifugal Fans, DX Evaporator Coils, and Refrigeration and control systems, for N+1 operation Each unit installed with: - ECM axial fans for heat rejection - ECM centrifugal fans for supply air with gravity fall backdraft dampers - One fixed, scroll and one digital, scroll compressor per circuit - Microchannel coils - Evaporator coils - Hot gas reheat coils (10KW/ea for 60T) - 2” MERV8 return air filters - Control panel with 65kAIC disconnect - Carel controller - R454b refrigerant | EA | EA |  | TRUE |  | P | ALL | DAYTON
135485 | 4 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 109 | 0 | 109 | 1410.33 | 153725.97 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.750X4 | C110 HH COPPER BUS BAR 3/4" X 4" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 3/4" X 4" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | Dayton
135485 | 3 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 209 | 0 | 209 | 1057.8 | 221080.2 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.375X6 | C110 HH COPPER BUS BAR 3/8" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 3/8" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | Dayton
135485 | 2 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-04T00:00:00 | 2026-11-04T00:00:00 | 417 | 0 | 417 | 705.17 | 294055.89 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.375X4 | C110 HH COPPER BUS BAR 3/8" X 4" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 3/8" X 4" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | Dayton
135485 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 750 | 0 | 750 | 528.85 | 396637.5 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.375X3 | C110 HH COPPER BUS BAR 3/8" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 3/8" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | Dayton
135484 | 5 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 250 | 0 | 250 | 1057.8 | 264450 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.375X6 | C110 HH COPPER BUS BAR 3/8" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 3/8" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | Dayton
135484 | 8 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 125 | 0 | 125 | 1410.33 | 176291.25 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.750X4 | C110 HH COPPER BUS BAR 3/4" X 4" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 3/4" X 4" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | Dayton
135484 | 4 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 209 | 0 | 209 | 705.17 | 147380.53 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.375X4 | C110 HH COPPER BUS BAR 3/8" X 4" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 3/8" X 4" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | Dayton
135484 | 2 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-10-19T00:00:00 | 2026-10-19T00:00:00 | 500 | 0 | 500 | 528.85 | 264425 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.375X3 | C110 HH COPPER BUS BAR 3/8" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 3/8" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | Dayton
132441 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-04-13T00:00:00 | 2026-09-21T00:00:00 | 2026-05-27T00:00:00 | 17 | 0 | 17 | 1410.33 | 23975.61 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.750X4 | C110 HH COPPER BUS BAR 3/4" X 4" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 3/4" X 4" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
136155 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-09-16T00:00:00 | 2026-10-14T00:00:00 | 2026-10-14T00:00:00 | 125 | 0 | 125 | 470.15 | 58768.75 | 55316 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB1-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - SILVER WASHED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - SILVER WASHED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-03T00:00:00 | 2026-11-03T00:00:00 | 460 | 0 | 460 | 235.022 | 108110.12 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 2 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-10T00:00:00 | 2026-11-10T00:00:00 | 460 | 0 | 460 | 235.022 | 108110.12 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 7 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-18T00:00:00 | 2026-11-18T00:00:00 | 542 | 0 | 542 | 352.6344 | 191127.84 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X3 | C110 HH COPPER BUS BAR 1/4" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 10 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-12T00:00:00 | 2026-11-12T00:00:00 | 521 | 0 | 521 | 470.1454 | 244945.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 9 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-05T00:00:00 | 2026-11-05T00:00:00 | 521 | 0 | 521 | 470.1454 | 244945.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 8 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-25T00:00:00 | 2026-11-25T00:00:00 | 542 | 0 | 542 | 352.6344 | 191127.84 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X3 | C110 HH COPPER BUS BAR 1/4" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 12 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-25T00:00:00 | 2026-11-25T00:00:00 | 521 | 0 | 521 | 470.1454 | 244945.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 17 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-03T00:00:00 | 2026-11-03T00:00:00 | 417 | 0 | 417 | 705.17 | 294055.89 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X6 | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 18 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-10T00:00:00 | 2026-11-10T00:00:00 | 417 | 0 | 417 | 705.17 | 294055.89 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X6 | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 16 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-23T00:00:00 | 2026-11-23T00:00:00 | 417 | 0 | 417 | 587.6564 | 245052.72 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X5 | C110 HH COPPER BUS BAR 1/4" X 5" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 5" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 15 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-16T00:00:00 | 2026-11-16T00:00:00 | 417 | 0 | 417 | 587.6564 | 245052.72 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X5 | C110 HH COPPER BUS BAR 1/4" X 5" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 5" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 5 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-04T00:00:00 | 2026-11-04T00:00:00 | 542 | 0 | 542 | 352.6344 | 191127.84 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X3 | C110 HH COPPER BUS BAR 1/4" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 3 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-17T00:00:00 | 2026-11-17T00:00:00 | 460 | 0 | 460 | 235.022 | 108110.12 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 14 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 417 | 0 | 417 | 587.6564 | 245052.72 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X5 | C110 HH COPPER BUS BAR 1/4" X 5" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 5" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 13 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 417 | 0 | 417 | 587.6564 | 245052.72 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X5 | C110 HH COPPER BUS BAR 1/4" X 5" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 5" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 19 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-17T00:00:00 | 2026-11-17T00:00:00 | 417 | 0 | 417 | 705.17 | 294055.89 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X6 | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 6 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-11T00:00:00 | 2026-11-11T00:00:00 | 542 | 0 | 542 | 352.6344 | 191127.84 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X3 | C110 HH COPPER BUS BAR 1/4" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 4 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-24T00:00:00 | 2026-11-24T00:00:00 | 460 | 0 | 460 | 235.022 | 108110.12 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135486 | 11 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-11-19T00:00:00 | 2026-11-19T00:00:00 | 521 | 0 | 521 | 470.1454 | 244945.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 16 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-22T00:00:00 | 2026-09-22T00:00:00 | 625 | 0 | 625 | 470.15 | 293843.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 14 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-25T00:00:00 | 2026-09-08T00:00:00 | 625 | 0 | 625 | 470.15 | 293843.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 4 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-28T00:00:00 | 2026-09-28T00:00:00 | 125 | 0 | 125 | 117.51 | 14688.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X1 | C110 HH COPPER BUS BAR 1/4" X 1" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 1" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 24 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-23T00:00:00 | 2026-09-23T00:00:00 | 625 | 0 | 625 | 705.17 | 440731.25 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X6 | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 7 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-21T00:00:00 | 2026-09-21T00:00:00 | 313 | 0 | 313 | 235.02 | 73561.26 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 21 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 500 | 0 | 500 | 587.66 | 293830 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X5 | C110 HH COPPER BUS BAR 1/4" X 5" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 5" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 25 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-30T00:00:00 | 2026-09-30T00:00:00 | 625 | 0 | 625 | 705.17 | 440731.25 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X6 | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 5 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-22T00:00:00 | 2026-09-07T00:00:00 | 313 | 0 | 313 | 235.02 | 73561.26 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 9 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-22T00:00:00 | 2026-09-07T00:00:00 | 300 | 0 | 300 | 293.83 | 88149 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X2.5 | C110 HH COPPER BUS BAR 1/4" X 2.5" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2.5" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 12 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-18T00:00:00 | 2026-09-21T00:00:00 | 625 | 0 | 625 | 343.6391 | 214774.44 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X3 | C110 HH COPPER BUS BAR 1/4" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 3" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 23 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-16T00:00:00 | 2026-09-16T00:00:00 | 625 | 0 | 625 | 705.17 | 440731.25 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X6 | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 8 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-28T00:00:00 | 2026-09-28T00:00:00 | 313 | 0 | 313 | 235.02 | 73561.26 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 17 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-29T00:00:00 | 2026-09-29T00:00:00 | 625 | 0 | 625 | 470.15 | 293843.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 2 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-10-02T00:00:00 | 2026-09-14T00:00:00 | 125 | 0 | 125 | 117.51 | 14688.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X1 | C110 HH COPPER BUS BAR 1/4" X 1" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 1" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 3 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-21T00:00:00 | 2026-09-21T00:00:00 | 125 | 0 | 125 | 117.51 | 14688.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X1 | C110 HH COPPER BUS BAR 1/4" X 1" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 1" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 6 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-25T00:00:00 | 2026-09-14T00:00:00 | 313 | 0 | 313 | 235.02 | 73561.26 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-21T00:00:00 | 2026-09-07T00:00:00 | 125 | 0 | 125 | 117.51 | 14688.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X1 | C110 HH COPPER BUS BAR 1/4" X 1" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 1" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133788 | 15 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-28T00:00:00 | 2026-09-15T00:00:00 | 625 | 0 | 625 | 470.15 | 293843.75 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
132570 | 4 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-04-17T00:00:00 | 2026-11-20T00:00:00 | 2026-11-20T00:00:00 | 159 | 0 | 159 | 227.493 | 36171.39 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB1-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #1) ROUND EDGE - SILVER WASHED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #1) ROUND EDGE - SILVER WASHED | FT | L12 |  | TRUE |  | P | PPD | Dayton
132570 | 5 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-04-17T00:00:00 | 2026-12-18T00:00:00 | 2026-12-18T00:00:00 | 159 | 0 | 159 | 227.493 | 36171.39 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB1-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #1) ROUND EDGE - SILVER WASHED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #1) ROUND EDGE - SILVER WASHED | FT | L12 |  | TRUE |  | P | PPD | Dayton
132570 | 6 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-04-17T00:00:00 | 2027-01-25T00:00:00 | 2027-01-25T00:00:00 | 32 | 0 | 32 | 227.493 | 7279.78 | 55369-6417 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB1-.250X2 | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #1) ROUND EDGE - SILVER WASHED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2" X 12' - #1) ROUND EDGE - SILVER WASHED | FT | L12 |  | TRUE |  | P | PPD | Dayton
135483 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 42 | 0 | 42 | 940.29 | 39492.18 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X8 | C110 HH COPPER BUS BAR 1/4" X 8" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 8" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135483 | 2 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 42 | 0 | 42 | 1762.97 | 74044.74 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.625X6 | C110 HH COPPER BUS BAR 5/8" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 5/8" X 6" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135483 | 4 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 209 | 0 | 209 | 293.83 | 61410.47 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X2.5 | C110 HH COPPER BUS BAR 1/4" X 2.5" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 2.5" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135483 | 3 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-08-14T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 709 | 0 | 709 | 117.51 | 83314.59 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X1 | C110 HH COPPER BUS BAR 1/4" X 1" X 12' - #3) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 1" X 12' - #3) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133787 | 16 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-18T00:00:00 | 2026-08-17T00:00:00 | 500 | 0 | 500 | 470.15 | 235075 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
133787 | 17 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-06-02T00:00:00 | 2026-09-18T00:00:00 | 2026-08-24T00:00:00 | 500 | 0 | 500 | 470.15 | 235075 | 55316-3157 | USA | N60 | 2098 | S+S INDUSTRIES INC | 77011 | CUB3-.250X4 | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | BUSB | C110 HH COPPER BUS BAR 1/4" X 4" X 12' - #1) ROUND EDGE - TIN PLATED | FT | L12 |  | TRUE |  | P | PPD | 100
135608 | 1 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-08-19T00:00:00 | 2026-11-06T00:00:00 | 2026-11-06T00:00:00 | 27 | 0 | 27 | 2900 | 78300 | 55369 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | ATS100514 | 5KVA, Single phase Control Power Transformers Input 24,940 V, +/-2 x 2.5% taps, 60 Hz, 125 kV BIL Sealed HV winding Output 120/240 V Copper/Aluminum wound, 200 C UL insl system, 80 C rise | PUR | 5KVA, Single phase Control Power Transformers Input 24,940 V, +/-2 x 2.5% taps, 60 Hz, 125 kV BIL Sealed HV winding Output 120/240 V Copper/Aluminum wound, 200 C UL insl system, 80 C rise | EA | EA |  | TRUE |  | P | PPD | DAYTON
133291 | 2 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-05-14T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 6 | 0 | 6 | 5950 | 35700 | 55369-6417 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | Q4170 | 15 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | PUR | 15 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | EA | EA |  | TRUE |  | P | PPD | DAYTON
133291 | 1 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-05-14T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 34 | 0 | 34 | 2750 | 93500 | 55369-6417 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | ATS100514 | 5KVA, Single phase Control Power Transformers Input 24,940 V, +/-2 x 2.5% taps, 60 Hz, 125 kV BIL Sealed HV winding Output 120/240 V Copper/Aluminum wound, 200 C UL insl system, 80 C rise | PUR | 5KVA, Single phase Control Power Transformers Input 24,940 V, +/-2 x 2.5% taps, 60 Hz, 125 kV BIL Sealed HV winding Output 120/240 V Copper/Aluminum wound, 200 C UL insl system, 80 C rise | EA | EA |  | TRUE |  | P | PPD | DAYTON
134757 | 2 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-07-14T00:00:00 | 2026-10-09T00:00:00 | 2026-10-09T00:00:00 | 1 | 0 | 1 | 5250 | 5250 | 55369-6417 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | ATS101508 | 15KVA, Single phase Control Power Transformers Input 24,940 V, +/-2 x 2.5% taps, 60 Hz, 125 kV BIL Sealed HV winding Output 120/240 V Copper/Aluminum wound, 200 C UL insl system, 80 C rise | PUR | 15KVA, Single phase Control Power Transformers Input 24,940 V, +/-2 x 2.5% taps, 60 Hz, 125 kV BIL Sealed HV winding Output 120/240 V Copper/Aluminum wound, 200 C UL insl system, 80 C rise | EA | EA |  | TRUE |  | P | PPD | DAYTON
134757 | 1 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-07-14T00:00:00 | 2026-10-05T00:00:00 | 2026-10-05T00:00:00 | 11 | 0 | 11 | 2750 | 30250 | 55369-6417 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | ATS100514 | 5KVA, Single phase Control Power Transformers Input 24,940 V, +/-2 x 2.5% taps, 60 Hz, 125 kV BIL Sealed HV winding Output 120/240 V Copper/Aluminum wound, 200 C UL insl system, 80 C rise | PUR | 5KVA, Single phase Control Power Transformers Input 24,940 V, +/-2 x 2.5% taps, 60 Hz, 125 kV BIL Sealed HV winding Output 120/240 V Copper/Aluminum wound, 200 C UL insl system, 80 C rise | EA | EA |  | TRUE |  | P | PPD | DAYTON
133943 | 1 | 3 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-01-25T00:00:00 | 2027-01-25T00:00:00 | 12 | 0 | 12 | 0 | 0 | 55369-6417 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | ATS101013 | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | PUR | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | EA | EA |  | TRUE |  | P | PPD | DAYTON
133943 | 1 | 6 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-04-26T00:00:00 | 2027-04-26T00:00:00 | 6 | 0 | 6 | 0 | 0 | 55369-6417 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | ATS101013 | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | PUR | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | EA | EA |  | TRUE |  | P | PPD | DAYTON
133943 | 1 | 5 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-03-25T00:00:00 | 2027-03-25T00:00:00 | 12 | 0 | 12 | 0 | 0 | 55369-6417 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | ATS101013 | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | PUR | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | EA | EA |  | TRUE |  | P | PPD | DAYTON
133943 | 1 | 2 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2026-12-23T00:00:00 | 2026-12-23T00:00:00 | 12 | 0 | 12 | 0 | 0 | 55369-6417 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | ATS101013 | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | PUR | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | EA | EA |  | TRUE |  | P | PPD | DAYTON
133943 | 1 | 4 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 12 | 0 | 12 | 0 | 0 | 55369-6417 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | ATS101013 | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | PUR | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | EA | EA |  | TRUE |  | P | PPD | DAYTON
133943 | 1 | 1 | States | Dayton | Taylor Barrett | TRUE | 2026-06-08T00:00:00 | 2026-11-20T00:00:00 | 2026-11-20T00:00:00 | 12 | 0 | 12 | 0 | 0 | 55369-6417 | USA | N30 | 2103 | SPEC-MAG SPECIALITY MAGNETICS LLC | 44056 | ATS101013 | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | PUR | 10 kVA 1 PH CPT 34.5 kV class Input 19.9 kV, 60 Hz, 150 kV BIL Output 120/240 V | EA | EA |  | TRUE |  | P | PPD | DAYTON
135667 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 6 | 0 | 6 | 52.2 | 313.2 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S125-50:5A | Current Transformers, 100:5, 4.72" x 3.94" with 1.26" Dia. Window | PUR | Current Transformers, 100:5, 4.72" x 3.94" with 1.26" Dia. Window | EA | EA |  | TRUE |  | P | PPD | 100
135667 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 30 | 0 | 30 | 33 | 990 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-100:5A | Current Transformers, 100:5, 3.27" x 3.78" with 1.65" Dia. Window | PUR | Current Transformers, 100:5, 3.27" x 3.78" with 1.65" Dia. Window | EA | EA |  | TRUE |  | P | PPD | 100
135667 | 8 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-03-29T00:00:00 | 2027-03-29T00:00:00 | 183 | 0 | 183 | 111.75 | 20450.25 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-2500:5A | Current Transformers, 2500:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 2500:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
135667 | 6 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 6 | 0 | 6 | 39.6 | 237.6 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-800:5A | Current Transformers, 800:5, 3.27" x 3.78" with 1.65" Dia. Window | PUR | Current Transformers, 800:5, 3.27" x 3.78" with 1.65" Dia. Window | EA | EA |  | TRUE |  | P | PPD | 100
135667 | 7 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-03-29T00:00:00 | 2027-03-29T00:00:00 | 60 | 0 | 60 | 102.81 | 6168.6 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-2000:5A | Current Transformers, 2000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 2000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
135667 | 5 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 75 | 0 | 75 | 33 | 2475 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-400:5A | Current Transformers, 400:5, 3.27" x 3.78" with 1.65" Dia. window | PUR | Current Transformers, 400:5, 3.27" x 3.78" with 1.65" Dia. window | EA | EA |  | TRUE |  | P | PPD | 100
135667 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-03-29T00:00:00 | 2027-03-29T00:00:00 | 165 | 0 | 165 | 42.9 | 7078.5 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-1000:5A | Current Transformers, 1000:5, 3.27" x 3.78" with 1.65" Dia. window | PUR | Current Transformers, 1000:5, 3.27" x 3.78" with 1.65" Dia. window | EA | EA |  | TRUE |  | P | PPD | 100
135667 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-03-29T00:00:00 | 2027-03-29T00:00:00 | 57 | 0 | 57 | 33 | 1881 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-300:5A | Current Transformers, 300:5, 3.27" x 3.78" with 1.65" Dia. Window | PUR | Current Transformers, 300:5, 3.27" x 3.78" with 1.65" Dia. Window | EA | EA |  | TRUE |  | P | PPD | 100
133346 | 1 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-05-18T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 30 | 0 | 30 | 42.9 | 5276.7 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-1000:5A | Current Transformers, 1000:5, 3.27" x 3.78" with 1.65" Dia. window | PUR | Current Transformers, 1000:5, 3.27" x 3.78" with 1.65" Dia. window | EA | EA |  | TRUE |  | P | PPD | 100
135636 | 5 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 30 | 0 | 30 | 33 | 3465 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-400:5A | Current Transformers, 400:5, 3.27" x 3.78" with 1.65" Dia. window | PUR | Current Transformers, 400:5, 3.27" x 3.78" with 1.65" Dia. window | EA | EA |  | TRUE |  | P | PPD | 100
135636 | 4 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-11-19T00:00:00 | 2026-11-19T00:00:00 | 123 | 0 | 123 | 33 | 4851 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-300:5A | Current Transformers, 300:5, 3.27" x 3.78" with 1.65" Dia. Window | PUR | Current Transformers, 300:5, 3.27" x 3.78" with 1.65" Dia. Window | EA | EA |  | TRUE |  | P | PPD | 100
135636 | 3 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-11-25T00:00:00 | 2026-11-25T00:00:00 | 300 | 0 | 300 | 42.9 | 15830.1 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-1000:5A | Current Transformers, 1000:5, 3.27" x 3.78" with 1.65" Dia. window | PUR | Current Transformers, 1000:5, 3.27" x 3.78" with 1.65" Dia. window | EA | EA |  | TRUE |  | P | PPD | 100
135636 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-09-10T00:00:00 | 2026-09-10T00:00:00 | 30 | 0 | 30 | 33 | 990 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-100:5A | Current Transformers, 100:5, 3.27" x 3.78" with 1.65" Dia. Window | PUR | Current Transformers, 100:5, 3.27" x 3.78" with 1.65" Dia. Window | EA | EA |  | TRUE |  | P | PPD | 100 | 2026-08-25T00:00:00
135636 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-09-10T00:00:00 | 2026-09-10T00:00:00 | 6 | 0 | 6 | 52.2 | 313.2 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S125-50:5A | Current Transformers, 100:5, 4.72" x 3.94" with 1.26" Dia. Window | PUR | Current Transformers, 100:5, 4.72" x 3.94" with 1.26" Dia. Window | EA | EA |  | TRUE |  | P | PPD | 100 | 2026-08-25T00:00:00
135636 | 8 | 4 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-11-25T00:00:00 | 2026-11-25T00:00:00 | 288 | 0 | 288 | 111.75 | 66267.75 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-2500:5A | Current Transformers, 2500:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 2500:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100 | 2026-11-25T00:00:00
135636 | 8 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 144 | 0 | 144 | 111.75 | 66267.75 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-2500:5A | Current Transformers, 2500:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 2500:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100 | 2026-09-24T00:00:00
135636 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 69 | 0 | 69 | 42.9 | 15830.1 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-1000:5A | Current Transformers, 1000:5, 3.27" x 3.78" with 1.65" Dia. window | PUR | Current Transformers, 1000:5, 3.27" x 3.78" with 1.65" Dia. window | EA | EA |  | TRUE |  | P | PPD | 100
135636 | 8 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-09-18T00:00:00 | 2026-09-18T00:00:00 | 82 | 0 | 82 | 111.75 | 66267.75 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-2500:5A | Current Transformers, 2500:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 2500:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100 | 2026-08-25T00:00:00
135636 | 5 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-11-25T00:00:00 | 2026-11-25T00:00:00 | 75 | 0 | 75 | 33 | 3465 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-400:5A | Current Transformers, 400:5, 3.27" x 3.78" with 1.65" Dia. window | PUR | Current Transformers, 400:5, 3.27" x 3.78" with 1.65" Dia. window | EA | EA |  | TRUE |  | P | PPD | 100
135636 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 24 | 0 | 24 | 33 | 4851 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-300:5A | Current Transformers, 300:5, 3.27" x 3.78" with 1.65" Dia. Window | PUR | Current Transformers, 300:5, 3.27" x 3.78" with 1.65" Dia. Window | EA | EA |  | TRUE |  | P | PPD | 100
135636 | 7 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-20T00:00:00 | 2026-11-25T00:00:00 | 2026-11-25T00:00:00 | 21 | 0 | 21 | 102.81 | 2159.01 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-2000:5A | Current Transformers, 2000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 2000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
136050 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-08T00:00:00 | 2026-10-08T00:00:00 | 324 | 0 | 324 | 7.2 | 6998.4 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | ACUBRAC-S3 | ACCUENERGY : OPTIONAL MOUNTING BRACKET KIT DESIGNED SPECIFICALLY FOR THE S433 SOLID-CORE CURRENT TRANSFORMER | PUR | ACCUENERGY : OPTIONAL MOUNTING BRACKET KIT DESIGNED SPECIFICALLY FOR THE S433 SOLID-CORE CURRENT TRANSFORMER | EA | EA |  | TRUE |  | P | PPD | 100
136050 | 2 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 324 | 0 | 324 | 81.9 | 79606.8 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S433-2000:5A | ACCUENERGY : CURRENT TRANSFORMER (CT), SOLID-CORE, 2000A:5A, CLASS 0.2, Ø93 MM WINDOW, UL LISTED. | PUR | ACCUENERGY : CURRENT TRANSFORMER (CT), SOLID-CORE, 2000A:5A, CLASS 0.2, Ø93 MM WINDOW, UL LISTED. | EA | EA |  | TRUE |  | P | PPD | 100
136050 | 1 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 324 | 0 | 324 | 7.2 | 6998.4 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | ACUBRAC-S3 | ACCUENERGY : OPTIONAL MOUNTING BRACKET KIT DESIGNED SPECIFICALLY FOR THE S433 SOLID-CORE CURRENT TRANSFORMER | PUR | ACCUENERGY : OPTIONAL MOUNTING BRACKET KIT DESIGNED SPECIFICALLY FOR THE S433 SOLID-CORE CURRENT TRANSFORMER | EA | EA |  | TRUE |  | P | PPD | 100
136050 | 2 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-11-10T00:00:00 | 2026-11-10T00:00:00 | 324 | 0 | 324 | 81.9 | 79606.8 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S433-2000:5A | ACCUENERGY : CURRENT TRANSFORMER (CT), SOLID-CORE, 2000A:5A, CLASS 0.2, Ø93 MM WINDOW, UL LISTED. | PUR | ACCUENERGY : CURRENT TRANSFORMER (CT), SOLID-CORE, 2000A:5A, CLASS 0.2, Ø93 MM WINDOW, UL LISTED. | EA | EA |  | TRUE |  | P | PPD | 100
136050 | 1 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-11-10T00:00:00 | 2026-11-10T00:00:00 | 324 | 0 | 324 | 7.2 | 6998.4 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | ACUBRAC-S3 | ACCUENERGY : OPTIONAL MOUNTING BRACKET KIT DESIGNED SPECIFICALLY FOR THE S433 SOLID-CORE CURRENT TRANSFORMER | PUR | ACCUENERGY : OPTIONAL MOUNTING BRACKET KIT DESIGNED SPECIFICALLY FOR THE S433 SOLID-CORE CURRENT TRANSFORMER | EA | EA |  | TRUE |  | P | PPD | 100
136050 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-11T00:00:00 | 2026-10-08T00:00:00 | 2026-10-08T00:00:00 | 324 | 0 | 324 | 81.9 | 79606.8 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S433-2000:5A | ACCUENERGY : CURRENT TRANSFORMER (CT), SOLID-CORE, 2000A:5A, CLASS 0.2, Ø93 MM WINDOW, UL LISTED. | PUR | ACCUENERGY : CURRENT TRANSFORMER (CT), SOLID-CORE, 2000A:5A, CLASS 0.2, Ø93 MM WINDOW, UL LISTED. | EA | EA |  | TRUE |  | P | PPD | 100
133046 | 1 | 5 | States | Champlin | Andrew Olson | TRUE | 2026-05-07T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 135 | 0 | 135 | 89.4 | 119080.8 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-4000:5A | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
133090 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-08T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 6 | 0 | 6 | 89.4 | 536.4 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-4000:5A | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
133651 | 2 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-05-27T00:00:00 | 2026-12-22T00:00:00 |  | 60 | 0 | 60 | 89.4 | 14661.6 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-4000:5A | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
133651 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-27T00:00:00 | 2026-10-26T00:00:00 |  | 104 | 0 | 104 | 89.4 | 14661.6 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-4000:5A | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
136237 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-21T00:00:00 | 2026-09-28T00:00:00 |  | 131 | 0 | 131 | 144 | 108720 | 55369 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-4161R-2000:333mV | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | PUR | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | EA | EA |  | FALSE |  | P | PPD | DAYTON | 2026-09-28T00:00:00
136237 | 1 | 4 | States | Dayton | Andrew Olson | TRUE | 2026-09-21T00:00:00 | 2026-11-09T00:00:00 |  | 144 | 0 | 144 | 144 | 108720 | 55369 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-4161R-2000:333mV | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | PUR | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | EA | EA |  | FALSE |  | P | PPD | DAYTON | 2026-11-09T00:00:00
136237 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-09-21T00:00:00 | 2026-10-12T00:00:00 |  | 144 | 0 | 144 | 144 | 108720 | 55369 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-4161R-2000:333mV | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | PUR | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | EA | EA |  | FALSE |  | P | PPD | DAYTON | 2026-10-12T00:00:00
136237 | 1 | 5 | States | Dayton | Andrew Olson | TRUE | 2026-09-21T00:00:00 | 2026-11-19T00:00:00 |  | 192 | 0 | 192 | 144 | 108720 | 55369 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-4161R-2000:333mV | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | PUR | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | EA | EA |  | FALSE |  | P | PPD | DAYTON | 2026-11-19T00:00:00
136237 | 1 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-09-21T00:00:00 | 2026-10-26T00:00:00 |  | 144 | 0 | 144 | 144 | 108720 | 55369 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-4161R-2000:333mV | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | PUR | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | EA | EA |  | FALSE |  | P | PPD | DAYTON | 2026-10-26T00:00:00
134073 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-06-15T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 6 | 0 | 6 | 102.81 | 616.86 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-2000:5A | Current Transformers, 2000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 2000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
134073 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-06-15T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 123 | 0 | 123 | 42.9 | 5276.7 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-1000:5A | Current Transformers, 1000:5, 3.27" x 3.78" with 1.65" Dia. window | PUR | Current Transformers, 1000:5, 3.27" x 3.78" with 1.65" Dia. window | EA | EA |  | TRUE |  | P | PPD | 100
135856 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-02T00:00:00 | 2026-12-28T00:00:00 | 2026-12-28T00:00:00 | 957 | 0 | 957 | 62.4 | 116812.8 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-3135R-800:5A | Current Transformers, 800:5, 5.67" x 6.10" with 3.10" x 3.50" window | PUR | Current Transformers, 800:5, 5.67" x 6.10" with 3.10" x 3.50" window | EA | EA |  | TRUE |  | P | PPD | 100
135856 | 1 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-09-02T00:00:00 | 2027-01-15T00:00:00 | 2027-01-15T00:00:00 | 915 | 0 | 915 | 62.4 | 116812.8 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-3135R-800:5A | Current Transformers, 800:5, 5.67" x 6.10" with 3.10" x 3.50" window | PUR | Current Transformers, 800:5, 5.67" x 6.10" with 3.10" x 3.50" window | EA | EA |  | TRUE |  | P | PPD | 100
134363 | 1 | 4 | States | Champlin | Andrew Olson | TRUE | 2026-06-25T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 228 | 0 | 228 | 144 | 131760 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-4161R-2000:333mV | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | PUR | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | EA | EA |  | TRUE |  | P | PPD | 100
134363 | 1 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-06-25T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 228 | 0 | 228 | 144 | 131760 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-4161R-2000:333mV | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | PUR | 2000:333MV REVENUE GRADE SPLIT CORE CT, 4.10" * 6.10" WINDOW SIZE | EA | EA |  | TRUE |  | P | PPD | 100
135177 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-03T00:00:00 | 2027-01-11T00:00:00 | 2027-01-11T00:00:00 | 88 | 0 | 88 | 89.4 | 7867.2 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-4000:5A | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
134878 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-07-20T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 130 | 0 | 130 | 89.4 | 11622 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-4000:5A | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
134289 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-06-23T00:00:00 | 2026-10-21T00:00:00 | 2026-10-21T00:00:00 | 10 | 0 | 10 | 63 | 630 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-3147-1200:5A | Current Transformers, 1200:5, 5.67” x 7.28” with 3.15” x 4.72” window | PUR | Current Transformers, 1200:5, 5.67” x 7.28” with 3.15” x 4.72” window | EA | EA |  | TRUE |  | P | PPD | 100
134289 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-06-23T00:00:00 | 2026-10-21T00:00:00 | 2026-10-21T00:00:00 | 21 | 0 | 21 | 33 | 693 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-300:5A | Current Transformers, 300:5, 3.27" x 3.78" with 1.65" Dia. Window | PUR | Current Transformers, 300:5, 3.27" x 3.78" with 1.65" Dia. Window | EA | EA |  | TRUE |  | P | PPD | 100
134289 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-06-23T00:00:00 | 2026-10-21T00:00:00 | 2026-10-21T00:00:00 | 21 | 0 | 21 | 89.4 | 1877.4 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-1200:5A | Current Transformers, 1200:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 1200:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
134289 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-06-23T00:00:00 | 2026-10-21T00:00:00 | 2026-10-21T00:00:00 | 9 | 0 | 9 | 89.4 | 804.6 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-800:5A | Current Transformers, 800:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 800:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
133384 | 1 | 4 | States | Champlin | Andrew Olson | TRUE | 2026-05-19T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 114 | 0 | 114 | 105 | 48195 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-3163-2000:5 | Current transformer, 2000:5 | PUR | Current transformer, 2000:5 | EA | EA |  | TRUE |  | P | PPD | 100
133384 | 1 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-05-19T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 114 | 0 | 114 | 105 | 48195 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-3163-2000:5 | Current transformer, 2000:5 | PUR | Current transformer, 2000:5 | EA | EA |  | TRUE |  | P | PPD | 100
133137 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-05-11T00:00:00 | 2026-09-24T00:00:00 | 2026-09-24T00:00:00 | 30 | 0 | 30 | 89.4 | 14751 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-4000:5A | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
133137 | 4 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-05-11T00:00:00 | 2026-10-26T00:00:00 | 2026-10-26T00:00:00 | 135 | 0 | 135 | 89.4 | 14751 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-4000:5A | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
134529 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-07-06T00:00:00 | 2026-10-16T00:00:00 |  | 3 | 0 | 3 | 138.57 | 415.71 | 55316-3157 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-4000:5A | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 4000:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
136160 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-16T00:00:00 | 2026-10-29T00:00:00 | 2026-10-29T00:00:00 | 110 | 0 | 110 | 89.4 | 9834 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S650-1200:5A | Current Transformers, 1200:5, 8.66" x 9.06" square with 6.30" x 6.30" window | PUR | Current Transformers, 1200:5, 8.66" x 9.06" square with 6.30" x 6.30" window | EA | EA |  | TRUE |  | P | PPD | 100
136160 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-16T00:00:00 | 2026-10-29T00:00:00 | 2026-10-29T00:00:00 | 100 | 0 | 100 | 33 | 3300 | 55316 | USA | N30 | 2110 | ACCUENERGY (CANADA) INC | M1L 2H6 | AcuCT-S165-200:5A | Current Transformers, 200:5, 3.27" x 3.78" with 1.65" Dia. Window | PUR | Current Transformers, 200:5, 3.27" x 3.78" with 1.65" Dia. Window | EA | EA |  | TRUE |  | P | PPD | 100
132049 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-03-25T00:00:00 | 2027-04-30T00:00:00 |  | 24 | 0 | 24 | 600000 | 14400000 | 55316-3157 | USA |  | 2122 | Sieyuan Electric USA,LLC | 75024 | DTCB-345 kV | LW58A-420/T2000A-50kA 1300 BIL Three-phase monopolar operation spring-motor operation with steel support structure with CT: two 2000:5 MR CT per bushing Accuracy class: C800 25mm/kV Control Voltage: 125VDC Auxiliary Voltage: 120VAC with the breaker poles discrepancy protection scheme Stainless Cabinet (Necessary for Breaker) Included. | PUR | LW58A-420/T2000A-50kA 1300 BIL Three-phase monopolar operation spring-motor operation with steel support structure with CT: two 2000:5 MR CT per bushing Accuracy class: C800 25mm/kV Control Voltage: 125VDC Auxiliary Voltage: 120VAC with the breaker poles discrepancy protection scheme Stainless Cabinet (Necessary for Breaker) Included. | EA | EA |  | TRUE |  | P | SPEC
132050 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-03-25T00:00:00 | 2027-02-26T00:00:00 | 2027-02-26T00:00:00 | 1 | 0 | 1 | 500000 | 500000 | 55316-3157 | USA | N30 | 2123 | Encompass Engineers and Architects | 45840 | Austin Data Center 345 kV Switch and Breaker QA/QC | QA/QC for (76) 345 kV Group Operated Switches & QA/QC for (24) 345 kV Power Circuit Breakers | Buy | QA/QC for (76) 345 kV Group Operated Switches & QA/QC for (24) 345 kV Power Circuit Breakers | EA | EA |  | TRUE |  | P | PPD
132051 | 1 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-03-25T00:00:00 | 2027-01-29T00:00:00 | 2027-01-29T00:00:00 | 6 | 0 | 6 | 89049 | 534294 | 55316-3157 | USA | N30 | 2124 | Springfield Electric Supply Company LLC dba ECHO | 62708 | 345TTR8-1300 | 345 KV TTR8 2000 AMP 1300 KV BIL W MO 345 KV, 1300 KV BIL, 2000 AMP, 100 KA MOM THREE POLE, GANG OPERATED TYPE TTR-8 ALUMINUM VERTICAL BREAK DISCONNECT SWITCH HORIZONTAL MOUNTING ARCING HORN POSITION INDICATORS MO-10 MOTOR OPERATING MECHANISM ALUMINUM HOUSING 30,000 IN-LBS OPERATING TORQUE 10.8 SEC OPERATING TIME 125 VDC CONTROLS FUSE PROTECTION ALLEN BRADLEY TERMINAL BLOCKS - STRIPPED WIRE TERMINATION 10 CIRCUIT AUX SWITCH FOR CUSTOMER USE 120 VAC THERMOSTATICALLY CONTROLLED HEATER W/ GUARD OPEN/CLOSE PUSHBUTTONS VARIABLE SPEED CONTROL INSULATORS: TR-324, STANDARD STRENGTH, CREEP, AND COLOR, WITH 5” B.C. TOP AND BOTTOM INCLUDED IN PRICE AND SHIPPED DIRECT TO JOBSITE, (9) PER SWITCH | PUR | 345 KV TTR8 2000 AMP 1300 KV BIL W MO 345 KV, 1300 KV BIL, 2000 AMP, 100 KA MOM THREE POLE, GANG OPERATED TYPE TTR-8 ALUMINUM VERTICAL BREAK DISCONNECT SWITCH HORIZONTAL MOUNTING ARCING HORN POSITION INDICATORS MO-10 MOTOR OPERATING MECHANISM ALUMINUM HOUSING 30,000 IN-LBS OPERATING TORQUE 10.8 SEC OPERATING TIME 125 VDC CONTROLS FUSE PROTECTION ALLEN BRADLEY TERMINAL BLOCKS - STRIPPED WIRE TERMINATION 10 CIRCUIT AUX SWITCH FOR CUSTOMER USE 120 VAC THERMOSTATICALLY CONTROLLED HEATER W/ GUARD OPEN/CLOSE PUSHBUTTONS VARIABLE SPEED CONTROL INSULATORS: TR-324, STANDARD STRENGTH, CREEP, AND COLOR, WITH 5” B.C. TOP AND BOTTOM INCLUDED IN PRICE AND SHIPPED DIRECT TO JOBSITE, (9) PER SWITCH | EA | EA |  | TRUE |  | P | B/W
132051 | 2 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-03-25T00:00:00 | 2027-01-29T00:00:00 | 2027-01-29T00:00:00 | 33 | 0 | 33 | 61957 | 4275033 | 55316-3157 | USA | N30 | 2124 | Springfield Electric Supply Company LLC dba ECHO | 62708 | 345TTR8-1300_ | 345 KV TTR8 2000 AMP-MANUAL WITH AUX CONTACTS | PUR | 345 KV TTR8 2000 AMP-MANUAL WITH AUX CONTACTS | EA | EA |  | TRUE |  | P | B/W | 100
132051 | 2 | 2 | States | Champlin | Megan Swymeler | TRUE | 2026-03-25T00:00:00 | 2027-02-26T00:00:00 | 2027-02-26T00:00:00 | 36 | 0 | 36 | 61957 | 4275033 | 55316-3157 | USA | N30 | 2124 | Springfield Electric Supply Company LLC dba ECHO | 62708 | 345TTR8-1300_ | 345 KV TTR8 2000 AMP-MANUAL WITH AUX CONTACTS | PUR | 345 KV TTR8 2000 AMP-MANUAL WITH AUX CONTACTS | EA | EA |  | TRUE |  | P | B/W | 100
132051 | 3 | 1 | States | Champlin | Megan Swymeler | TRUE | 2026-03-25T00:00:00 | 2027-01-29T00:00:00 | 2027-01-29T00:00:00 | 69 | 0 | 69 | 34987 | 2414103 | 55316-3157 | USA | N30 | 2124 | Springfield Electric Supply Company LLC dba ECHO | 62708 | SWITCH STAND WITH ENGINEERING | SWITCH STAND WITH ENGINEERING | PUR | SWITCH STAND WITH ENGINEERING | EA | EA |  | TRUE |  | P | B/W | 100
136141 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-15T00:00:00 | 2026-10-20T00:00:00 | 2026-10-20T00:00:00 | 12 | 0 | 12 | 1000 | 12000 | 55369 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | CT142-302 | "Electromagnetics Industries Current Transformer, #142 302: 600V, 10 kV BIL, 3000:5A Ratio, Metering and Relay, Class C200" | PUR | "Electromagnetics Industries Current Transformer, #142 302: 600V, 10 kV BIL, 3000:5A Ratio, Metering and Relay, Class C200" | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-10-05T00:00:00
136141 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-15T00:00:00 | 2026-10-20T00:00:00 | 2026-10-20T00:00:00 | 36 | 0 | 36 | 1000 | 36000 | 55369 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | CT780-302M | "Electromagnetics Industries Current Transformer, #780 302: 600V, 10 kV BIL, 3000:5A Ratio, Metering and Relay, Class C200" | PUR | "Electromagnetics Industries Current Transformer, #780 302: 600V, 10 kV BIL, 3000:5A Ratio, Metering and Relay, Class C200" | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-10-05T00:00:00
132860 | 1 | 10 | States | Dayton | Andrew Olson | TRUE | 2026-04-29T00:00:00 | 2026-08-21T00:00:00 | 2026-08-21T00:00:00 | 3 | 0 | 3 | 986.07 | 97620.93 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | 143-202 | 2000:5 SR CT for Bus Differential Protection (SEL-787) | PUR | 2000:5 SR CT for Bus Differential Protection (SEL-787) | EA | EA |  | TRUE |  | P | PPD | DAYTON
132860 | 6 | 14 | States | Dayton | Andrew Olson | TRUE | 2026-04-29T00:00:00 | 2026-09-18T00:00:00 | 2026-09-18T00:00:00 | 12 | 0 | 12 | 986.07 | 215949.33 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | 143-122MR | 200:5 MR CT for 1200A Breakers (SEL 751+SEL-735) | PUR | 200:5 MR CT for 1200A Breakers (SEL751+SEL-735) | EA | EA |  | TRUE |  | P | PPD | DAYTON
132860 | 4 | 7 | States | Dayton | Andrew Olson | TRUE | 2026-04-29T00:00:00 | 2026-08-14T00:00:00 | 2026-08-07T00:00:00 | 3 | 0 | 3 | 8500 | 204000 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | Q39826 | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | PUR | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | EA | EA |  | TRUE |  | P | PPD | DAYTON
132860 | 4 | 6 | States | Dayton | Andrew Olson | TRUE | 2026-04-29T00:00:00 | 2026-08-07T00:00:00 | 2026-07-31T00:00:00 | 3 | 1 | 2 | 8500 | 204000 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | Q39826 | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | PUR | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | EA | EA |  | TRUE |  | P | PPD | DAYTON
132860 | 1 | 9 | States | Dayton | Andrew Olson | TRUE | 2026-04-29T00:00:00 | 2026-08-14T00:00:00 | 2026-08-14T00:00:00 | 9 | 3 | 6 | 986.07 | 97620.93 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | 143-202 | 2000:5 SR CT for Bus Differential Protection (SEL-787) | PUR | 2000:5 SR CT for Bus Differential Protection (SEL-787) | EA | EA |  | TRUE |  | P | PPD | DAYTON
132860 | 4 | 8 | States | Dayton | Andrew Olson | TRUE | 2026-04-29T00:00:00 | 2026-08-21T00:00:00 | 2026-08-14T00:00:00 | 3 | 0 | 3 | 8500 | 204000 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | Q39826 | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | PUR | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | EA | EA |  | TRUE |  | P | PPD | DAYTON
134600 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-07-08T00:00:00 | 2026-08-10T00:00:00 |  | 6 | 0 | 6 | 8500 | 76500 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | Q39826 | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | PUR | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | EA | EA |  | TRUE |  | P | PPD | DAYTON
134600 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-07-08T00:00:00 | 2026-08-10T00:00:00 |  | 3 | 0 | 3 | 8500 | 76500 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | Q39826 | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | PUR | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | EA | EA |  | TRUE |  | P | PPD | DAYTON
134167 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-06-17T00:00:00 | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 | 2 | 0 | 2 | 8500 | 51000 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | Q39826 | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | PUR | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | EA | EA |  | TRUE |  | P | PPD | DAYTON
134167 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-06-17T00:00:00 | 2026-10-01T00:00:00 | 2026-10-01T00:00:00 | 2 | 0 | 2 | 8500 | 51000 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | Q39826 | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | PUR | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | EA | EA |  | TRUE |  | P | PPD | DAYTON
134167 | 1 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-06-17T00:00:00 | 2026-11-19T00:00:00 | 2026-11-19T00:00:00 | 2 | 0 | 2 | 8500 | 51000 | 55369-6417 | USA | N60 | 2136 | OLYMPIC CONTROLS CORP | 60103 | Q39826 | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | PUR | 25KVA Control Power Transformer, 1PH, 34500-120/240V, Class AA, 150kV BIL, Acutran | EA | EA |  | TRUE |  | P | PPD | DAYTON
135746 | 2 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-26T00:00:00 | 2026-09-24T00:00:00 |  | 1 | 0 | 1 | 2880 | 2880 | 55369 | USA | N60 | 2139 | Resa Service, LLC | 77064 | Circuit Breaker Injection Testing | 3rd Party Circuit Breaker Injection Testing | Buy | 3rd Party Circuit Breaker Injection Testing | EA | EA |  | FALSE |  | P | PPD
135746 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-26T00:00:00 | 2026-09-21T00:00:00 |  | 1 | 0 | 1 | 3840 | 3840 | 55369 | USA | N60 | 2139 | Resa Service, LLC | 77064 | Circuit Breaker Injection Testing | 3rd Party Circuit Breaker Injection Testing | Buy | 3rd Party Circuit Breaker Injection Testing | EA | EA |  | FALSE |  | P | PPD
135038 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-07-27T00:00:00 | 2026-12-15T00:00:00 |  | 12 | 10.06 | 1.94 | 3806.88 | 45682.56 | 55369-6417 | USA | N60 | 2139 | Resa Service, LLC | 77064 | Circuit Breaker Injection Testing | 3rd Party Circuit Breaker Injection Testing | Buy | 3rd Party Circuit Breaker Injection Testing | EA | EA |  | TRUE |  | P | PPD
132882 | 1 | 1 | States | Champlin | Robert Boulka | TRUE | 2026-04-30T00:00:00 |  |  | 100 | 44.97 | 55.03 | 3393.6 | 339360 | 55316-3157 | USA | N60 | 2139 | Resa Service, LLC | 77064 | Circuit Breaker Injection Testing | 3rd Party Circuit Breaker Injection Testing | Buy | 3rd Party Circuit Breaker Injection Testing | EA | EA |  | TRUE |  | P | PPD | 100
134005 | 2 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-10T00:00:00 | 2027-01-15T00:00:00 | 2027-01-15T00:00:00 | 3 | 0 | 3 | 125600 | 376800 | 55369-6417 | USA | N60 | 2147 | Safe Air Technologies Intermediate, LLC | 70814 | VIDD3-4MMU-R360ME-E10-5T-R | CUSTOM DESIGNED VERTICAL PACKAGE UNIT 25 TON, 460VAC SINGLE HOUSING CONSISTING OF 2 INDEPENDENT HVAC SYSTEMS SYSTEMS MECHANICALLY DIVIDED TO ALLOW FOR SAFETY ISOLATION OF ONE SYSTEM WHILE THE OTHER IS ACTIVE | PUR | CUSTOM DESIGNED VERTICAL PACKAGE UNIT 25 TON, 460VAC SINGLE HOUSING CONSISTING OF 2 INDEPENDENT HVAC SYSTEMS SYSTEMS MECHANICALLY DIVIDED TO ALLOW FOR SAFETY ISOLATION OF ONE SYSTEM WHILE THE OTHER IS ACTIVE | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-10-16T00:00:00
134005 | 1 | 1 | States | Dayton | Megan Swymeler | TRUE | 2026-06-10T00:00:00 | 2027-01-15T00:00:00 | 2027-01-15T00:00:00 | 3 | 0 | 3 | 2417.04 | 7251.12 | 55369-6417 | USA | N60 | 2147 | Safe Air Technologies Intermediate, LLC | 70814 | 728MC5300-C | Lead/Lag Controller | PUR | Lead/Lag Controller | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-10-16T00:00:00
134051 | 1 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-06-12T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 34 | 0 | 34 | 3714 | 605382 | 55316-3157 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 52-17.003 | 512-PRO 24VDC Connection | PUR | 512-PRO 24VDC Connection | EA | EA |  | TRUE |  | P | PPD | 100
134051 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-06-12T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 41 | 0 | 41 | 3714 | 605382 | 55316-3157 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 52-17.003 | 512-PRO 24VDC Connection | PUR | 512-PRO 24VDC Connection | EA | EA |  | TRUE |  | P | PPD | 100
134051 | 1 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-06-12T00:00:00 | 2026-11-09T00:00:00 | 2026-11-09T00:00:00 | 88 | 0 | 88 | 3714 | 605382 | 55316-3157 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 52-17.003 | 512-PRO 24VDC Connection | PUR | 512-PRO 24VDC Connection | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 5 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2026-12-14T00:00:00 | 2026-12-14T00:00:00 | 58 | 0 | 58 | 295 | 43955 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-DI14 | 800-DI14 Digital Input Module | PUR | 800-DI14 Digital Input Module | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 6 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-01-26T00:00:00 | 2027-01-26T00:00:00 | 34 | 0 | 34 | 255 | 44115 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | RD 96 | RD 96 remote display w/USB Cable | PUR | RD 96 remote display w/USB Cable | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 6 | 4 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-03-17T00:00:00 | 2027-03-17T00:00:00 | 34 | 0 | 34 | 255 | 44115 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | RD 96 | RD 96 remote display w/USB Cable | PUR | RD 96 remote display w/USB Cable | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 7 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2026-12-14T00:00:00 | 2026-12-14T00:00:00 | 34 | 0 | 34 | 1874 | 279226 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | UMG801 | UMG801 Expandable modular power analyzer | PUR | UMG801 Expandable modular power analyzer | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 5 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-02-03T00:00:00 | 2027-02-03T00:00:00 | 44 | 0 | 44 | 295 | 43955 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-DI14 | 800-DI14 Digital Input Module | PUR | 800-DI14 Digital Input Module | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 7 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-01-26T00:00:00 | 2027-01-26T00:00:00 | 34 | 0 | 34 | 1874 | 279226 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | UMG801 | UMG801 Expandable modular power analyzer | PUR | UMG801 Expandable modular power analyzer | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 85 | 0 | 85 | 461 | 113867 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-CT8-A | 800-CT8-A Current Measuring Module | PUR | 800-CT8-A Current Measuring Module | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2026-11-16T00:00:00 | 2026-11-16T00:00:00 | 49 | 0 | 49 | 154 | 23254 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-CON-RJ45 | 800-CON-RJ45 Communication Module with 2 sub-units | PUR | 800-CON-RJ45 Communication Module with 2 sub-units | EA | EA |  | TRUE |  | P | PPD | 100 | 2026-10-16T00:00:00
135669 | 5 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 47 | 0 | 47 | 295 | 43955 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-DI14 | 800-DI14 Digital Input Module | PUR | 800-DI14 Digital Input Module | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 4 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-02-03T00:00:00 | 2027-02-03T00:00:00 | 84 | 0 | 84 | 461 | 113867 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-CT8-A | 800-CT8-A Current Measuring Module | PUR | 800-CT8-A Current Measuring Module | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 3 | 4 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-03-17T00:00:00 | 2027-03-17T00:00:00 | 34 | 0 | 34 | 154 | 23254 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-CON-RJ45 | 800-CON-RJ45 Communication Module with 2 sub-units | PUR | 800-CON-RJ45 Communication Module with 2 sub-units | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 2 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 66 | 0 | 66 | 668 | 84836 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 5236002 | UMG 96-PQ-L 24VDC Connection | PUR | UMG 96-PQ-L 24VDC Connection | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 7 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 47 | 0 | 47 | 1874 | 279226 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | UMG801 | UMG801 Expandable modular power analyzer | PUR | UMG801 Expandable modular power analyzer | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-01-22T00:00:00 | 2027-01-22T00:00:00 | 61 | 0 | 61 | 668 | 84836 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 5236002 | UMG 96-PQ-L 24VDC Connection | PUR | UMG 96-PQ-L 24VDC Connection | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 7 | 4 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-03-17T00:00:00 | 2027-03-17T00:00:00 | 34 | 0 | 34 | 1874 | 279226 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | UMG801 | UMG801 Expandable modular power analyzer | PUR | UMG801 Expandable modular power analyzer | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 18 | 0 | 18 | 308 | 5544 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 5232010 | UMG 96-PQ-L Ethernet Expansion Module | PUR | UMG 96-PQ-L Ethernet Expansion Module | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 3 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2027-01-26T00:00:00 | 2027-01-26T00:00:00 | 34 | 0 | 34 | 154 | 23254 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-CON-RJ45 | 800-CON-RJ45 Communication Module with 2 sub-units | PUR | 800-CON-RJ45 Communication Module with 2 sub-units | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 6 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2026-11-02T00:00:00 | 2026-11-02T00:00:00 | 71 | 0 | 71 | 255 | 44115 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | RD 96 | RD 96 remote display w/USB Cable | PUR | RD 96 remote display w/USB Cable | EA | EA |  | TRUE |  | P | PPD | 100 | 2026-10-12T00:00:00
135669 | 4 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2026-12-14T00:00:00 | 2026-12-14T00:00:00 | 78 | 0 | 78 | 461 | 113867 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-CT8-A | 800-CT8-A Current Measuring Module | PUR | 800-CT8-A Current Measuring Module | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 6 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2026-12-21T00:00:00 | 2026-12-21T00:00:00 | 34 | 0 | 34 | 255 | 44115 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | RD 96 | RD 96 remote display w/USB Cable | PUR | RD 96 remote display w/USB Cable | EA | EA |  | TRUE |  | P | PPD | 100
135669 | 3 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-08-24T00:00:00 | 2026-12-14T00:00:00 | 2026-12-14T00:00:00 | 34 | 0 | 34 | 154 | 23254 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-CON-RJ45 | 800-CON-RJ45 Communication Module with 2 sub-units | PUR | 800-CON-RJ45 Communication Module with 2 sub-units | EA | EA |  | TRUE |  | P | PPD | 100
136069 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2027-05-25T00:00:00 | 2027-05-25T00:00:00 | 75 | 0 | 75 | 668 | 50100 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 5236002 | UMG 96-PQ-L 24VDC Connection | PUR | UMG 96-PQ-L 24VDC Connection | EA | EA |  | TRUE |  | P | PPD | 100
136069 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2027-01-22T00:00:00 | 2027-01-22T00:00:00 | 18 | 0 | 18 | 308 | 24332 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 5232010 | UMG 96-PQ-L Ethernet Expansion Module | PUR | UMG 96-PQ-L Ethernet Expansion Module | EA | EA |  | TRUE |  | P | PPD | 100
136069 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2027-05-25T00:00:00 | 2027-05-25T00:00:00 | 139 | 0 | 139 | 461 | 64079 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-CT8-A | 800-CT8-A Current Measuring Module | PUR | 800-CT8-A Current Measuring Module | EA | EA |  | TRUE |  | P | PPD | 100
136069 | 5 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2027-05-25T00:00:00 | 2027-05-25T00:00:00 | 81 | 0 | 81 | 295 | 23895 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-DI14 | 800-DI14 Digital Input Module | PUR | 800-DI14 Digital Input Module | EA | EA |  | TRUE |  | P | PPD | 100
136069 | 7 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2027-05-25T00:00:00 | 2027-05-25T00:00:00 | 81 | 0 | 81 | 1874 | 151794 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | UMG801 | UMG801 Expandable modular power analyzer | PUR | UMG801 Expandable modular power analyzer | EA | EA |  | TRUE |  | P | PPD | 100
136069 | 6 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2027-05-25T00:00:00 | 2027-05-25T00:00:00 | 57 | 0 | 57 | 255 | 14535 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | RD 96 | RD 96 remote display w/USB Cable | PUR | RD 96 remote display w/USB Cable | EA | EA |  | TRUE |  | P | PPD | 100
136069 | 1 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2027-02-09T00:00:00 | 2027-02-09T00:00:00 | 10 | 0 | 10 | 308 | 24332 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 5232010 | UMG 96-PQ-L Ethernet Expansion Module | PUR | UMG 96-PQ-L Ethernet Expansion Module | EA | EA |  | TRUE |  | P | PPD | 100
136069 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2027-05-25T00:00:00 | 2027-05-25T00:00:00 | 83 | 0 | 83 | 154 | 12782 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 800-CON-RJ45 | 800-CON-RJ45 Communication Module with 2 sub-units | PUR | 800-CON-RJ45 Communication Module with 2 sub-units | EA | EA |  | TRUE |  | P | PPD | 100
136069 | 1 | 3 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2027-02-22T00:00:00 | 2027-02-22T00:00:00 | 10 | 0 | 10 | 308 | 24332 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 5232010 | UMG 96-PQ-L Ethernet Expansion Module | PUR | UMG 96-PQ-L Ethernet Expansion Module | EA | EA |  | TRUE |  | P | PPD | 100
136069 | 1 | 4 | States | Champlin | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2027-05-25T00:00:00 | 2027-05-25T00:00:00 | 41 | 0 | 41 | 308 | 24332 | 55316 | USA | N60 | 2148 | JANITZA NORTH AMERICA LP | 20147 | 5232010 | UMG 96-PQ-L Ethernet Expansion Module | PUR | UMG 96-PQ-L Ethernet Expansion Module | EA | EA |  | TRUE |  | P | PPD | 100
133168 | 1 | 1 | States | Champlin | Holly Davis | TRUE | 2026-05-11T00:00:00 | 2026-10-06T00:00:00 | 2026-10-06T00:00:00 | 9 | 0 | 9 | 386 | 3474 | 55316-3157 | USA | N30 | 2151 | Meramec Instrument Transformer Company | 65453 | CRT-15E-152-NNN | CURRENT TRANSDUCER, METERING, 1500:5A, 0.15 ACCURACY | PUR | CURRENT TRANSDUCER, METERING, 1500:5A, 0.15 ACCURACY | EA | EA |  | TRUE |  | P | PPD | 100
135950 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-08T00:00:00 | 2026-10-23T00:00:00 |  | 2500 | 0 | 2500 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 3042117 | ST 2,5-TWIN/ 1P | PUR | ST 2,5-TWIN/ 1P | EA | EA |  | FALSE |  | P | PPD | 100
135950 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-08T00:00:00 | 2026-10-23T00:00:00 |  | 200 | 0 | 200 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 3045567 | UPR/ 2 - Latching | PUR | UPR/ 2 - Latching | EA | EA |  | FALSE |  | P | PPD | 100
135950 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-08T00:00:00 | 2026-10-23T00:00:00 |  | 50 | 0 | 50 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071735 | LP 2,5/1-R Plug | PUR | LP 2,5/1-R Plug | EA | EA |  | FALSE |  | P | PPD | 100
135992 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-10T00:00:00 | 2026-09-24T00:00:00 |  | 25 | 0 | 25 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071729 | LP 2,5/1-L Plug | PUR | LP 2,5/1-L Plug | EA | EA |  | FALSE |  | P | PPD | 100
135992 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-10T00:00:00 | 2026-10-23T00:00:00 |  | 150 | 0 | 150 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071732 | LP 2,5/1-M Plug | PUR | LP 2,5/1-M Plug | EA | EA |  | FALSE |  | P | PPD | 100
135992 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-10T00:00:00 | 2026-09-24T00:00:00 |  | 25 | 0 | 25 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071735 | LP 2,5/1-R Plug | PUR | LP 2,5/1-R Plug | EA | EA |  | FALSE |  | P | PPD | 100
135992 | 3 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-09-10T00:00:00 | 2026-10-23T00:00:00 |  | 50 | 0 | 50 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071735 | LP 2,5/1-R Plug | PUR | LP 2,5/1-R Plug | EA | EA |  | FALSE |  | P | PPD | 100
135992 | 1 | 2 | States | Champlin | Andrew Olson | TRUE | 2026-09-10T00:00:00 | 2026-10-23T00:00:00 |  | 50 | 0 | 50 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071729 | LP 2,5/1-L Plug | PUR | LP 2,5/1-L Plug | EA | EA |  | FALSE |  | P | PPD | 100
135992 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-10T00:00:00 | 2026-10-23T00:00:00 |  | 300 | 0 | 300 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 3042117 | ST 2,5-TWIN/ 1P | PUR | ST 2,5-TWIN/ 1P | EA | EA |  | FALSE |  | P | PPD | 100
135924 | 4 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-04T00:00:00 | 2026-10-23T00:00:00 |  | 50 | 0 | 50 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071729 | LP 2,5/1-L Plug | PUR | LP 2,5/1-L Plug | EA | EA |  | FALSE |  | P | PPD | 100
135924 | 3 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-04T00:00:00 | 2026-10-23T00:00:00 |  | 70 | 0 | 70 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071726 | LP 2,5/15-Plug | PUR | LP 2,5/15-Plug | EA | EA |  | FALSE |  | P | PPD | 100
135924 | 5 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-04T00:00:00 | 2026-10-23T00:00:00 |  | 300 | 0 | 300 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071732 | LP 2,5/1-M Plug | PUR | LP 2,5/1-M Plug | EA | EA |  | FALSE |  | P | PPD | 100
135924 | 1 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-04T00:00:00 | 2026-10-23T00:00:00 |  | 80 | 0 | 80 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071723 | LP 2,5/12-Plug | PUR | LP 2,5/12-Plug | EA | EA |  | FALSE |  | P | PPD | 100
135924 | 2 | 1 | States | Champlin | Andrew Olson | TRUE | 2026-09-04T00:00:00 | 2026-10-23T00:00:00 |  | 20 | 0 | 20 | 0 | 0 | 55316 | USA | N60 | 2154 | Capital Electric | 30384-4749 | 1071725 | LP 2,5/14-Plug | PUR | LP 2,5/14-Plug | EA | EA |  | FALSE |  | P | PPD | 100
135183 | 1 | 1 | States | Champlin | Taylor Barrett | TRUE | 2026-08-03T00:00:00 | 2026-09-02T00:00:00 | 2026-09-02T00:00:00 | 1 | 0 | 1 | 5000 | 5000 | 55316-3157 | USA | N60 | 2162 | Leonard Petroskey | 55746 | Startup & Commissioning | 3rd Party Startup & Commissioning | Buy | 3rd Party Startup & Commissioning | EA | EA |  | TRUE |  | P | PPD | 100
135155 | 1 | 10 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-10
135155 | 1 | 19 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-19
135155 | 1 | 13 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-13
135155 | 1 | 34 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-34
135155 | 1 | 36 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-36
135155 | 1 | 45 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-45
135155 | 1 | 31 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-31
135155 | 1 | 42 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-42
135155 | 1 | 26 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-26
135155 | 1 | 9 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-9
135155 | 1 | 29 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-29
135155 | 1 | 15 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-15
135155 | 1 | 41 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-41
135155 | 1 | 14 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-14
135155 | 1 | 4 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-4
135155 | 1 | 43 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-43
135155 | 2 | 1 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2026-11-11T00:00:00 |  | 1 | 0 | 1 | 118564 | 118564 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77446S-1
135155 | 1 | 44 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-44
135155 | 1 | 32 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-32
135155 | 1 | 5 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-5
135155 | 1 | 16 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-16
135155 | 1 | 22 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-22
135155 | 1 | 37 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-37
135155 | 1 | 25 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-25
135155 | 1 | 6 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-6
135155 | 1 | 17 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-17
135155 | 1 | 33 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-33
135155 | 1 | 12 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-12
135155 | 1 | 35 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-35
135155 | 1 | 21 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-21
135155 | 1 | 27 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-27
135155 | 1 | 18 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-18
135155 | 1 | 23 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-23
135155 | 1 | 7 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-7
135155 | 1 | 20 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-20
135155 | 1 | 24 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-24
135155 | 1 | 46 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-46
135155 | 1 | 8 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-8
135155 | 1 | 28 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-28
135155 | 1 | 1 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-1
135155 | 1 | 40 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-40
135155 | 1 | 39 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-39
135155 | 1 | 30 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-30
135155 | 1 | 2 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-2
135155 | 1 | 3 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-3
135155 | 1 | 47 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-47
135155 | 1 | 11 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-03-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-11
135155 | 1 | 38 | States | Dayton | Holly Davis | TRUE | 2026-08-03T00:00:00 | 2027-05-03T00:00:00 |  | 1 | 0 | 1 | 118564 | 5572508 | 55369-6417 | USA | N60 | 2165 | Intelligent Technologies & Services | 92821 | ROM-12.05.26 | FPS Phase 3 ROM - Fire Suppression System | PUR | FPS Phase 3 ROM - Fire Suppression System | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77445S-38
135520 | 1 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 5473.69 | 0 | 5473.69 | 14.48 | 376480 | 55369-6417 | USA | N30 | 2172 | Nucor Insulated Panel Group LLC | 75067 | TSUL-4.00-42X146.50 | Thermalsafe Panel TSUL Exterior Vertical 4.00 (Thermalsafe fire partition panels) | ORM | Thermalsafe Panel TSUL Exterior Vertical 4.00 (Thermalsafe fire partition panels) | EA | SF |  | TRUE |  | P | PPD | DAYTON
135520 | 2 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-09-24T00:00:00 | 2026-10-12T00:00:00 | 1700 | 0 | 1700 | 1.09 | 9265 | 55369-6417 | USA | N30 | 2172 | Nucor Insulated Panel Group LLC | 75067 | 343071 | 1148P.NPW¦ 1/4" - 14 x 6" HWH Type 3 SDS w/BN washer¦BRIGHT WHITE | PUR | 1148P.NPW¦ 1/4" - 14 x 6" HWH Type 3 SDS w/BN washer¦BRIGHT WHITE | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-09-08T00:00:00
135520 | 1 | 2 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-09-24T00:00:00 | 2026-10-12T00:00:00 | 5131.58 | 0 | 5131.58 | 14.48 | 376480 | 55369-6417 | USA | N30 | 2172 | Nucor Insulated Panel Group LLC | 75067 | TSUL-4.00-42X146.50 | Thermalsafe Panel TSUL Exterior Vertical 4.00 (Thermalsafe fire partition panels) | ORM | Thermalsafe Panel TSUL Exterior Vertical 4.00 (Thermalsafe fire partition panels) | EA | SF |  | TRUE |  | P | PPD | DAYTON
135520 | 1 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 5131.58 | 0 | 5131.58 | 14.48 | 376480 | 55369-6417 | USA | N30 | 2172 | Nucor Insulated Panel Group LLC | 75067 | TSUL-4.00-42X146.50 | Thermalsafe Panel TSUL Exterior Vertical 4.00 (Thermalsafe fire partition panels) | ORM | Thermalsafe Panel TSUL Exterior Vertical 4.00 (Thermalsafe fire partition panels) | EA | SF |  | TRUE |  | P | PPD | DAYTON
135520 | 1 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-09-24T00:00:00 | 2026-10-12T00:00:00 | 5131.58 | 0 | 5131.58 | 14.48 | 376480 | 55369-6417 | USA | N30 | 2172 | Nucor Insulated Panel Group LLC | 75067 | TSUL-4.00-42X146.50 | Thermalsafe Panel TSUL Exterior Vertical 4.00 (Thermalsafe fire partition panels) | ORM | Thermalsafe Panel TSUL Exterior Vertical 4.00 (Thermalsafe fire partition panels) | EA | SF |  | TRUE |  | P | PPD | DAYTON
135520 | 2 | 1 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-09-24T00:00:00 | 2026-10-12T00:00:00 | 1700 | 0 | 1700 | 1.09 | 9265 | 55369-6417 | USA | N30 | 2172 | Nucor Insulated Panel Group LLC | 75067 | 343071 | 1148P.NPW¦ 1/4" - 14 x 6" HWH Type 3 SDS w/BN washer¦BRIGHT WHITE | PUR | 1148P.NPW¦ 1/4" - 14 x 6" HWH Type 3 SDS w/BN washer¦BRIGHT WHITE | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-08-31T00:00:00
135520 | 1 | 5 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 5131.57 | 0 | 5131.57 | 14.48 | 376480 | 55369-6417 | USA | N30 | 2172 | Nucor Insulated Panel Group LLC | 75067 | TSUL-4.00-42X146.50 | Thermalsafe Panel TSUL Exterior Vertical 4.00 (Thermalsafe fire partition panels) | ORM | Thermalsafe Panel TSUL Exterior Vertical 4.00 (Thermalsafe fire partition panels) | EA | SF |  | TRUE |  | P | PPD | DAYTON
135520 | 2 | 3 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 1700 | 0 | 1700 | 1.09 | 9265 | 55369-6417 | USA | N30 | 2172 | Nucor Insulated Panel Group LLC | 75067 | 343071 | 1148P.NPW¦ 1/4" - 14 x 6" HWH Type 3 SDS w/BN washer¦BRIGHT WHITE | PUR | 1148P.NPW¦ 1/4" - 14 x 6" HWH Type 3 SDS w/BN washer¦BRIGHT WHITE | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-09-28T00:00:00
135520 | 2 | 4 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 1900 | 0 | 1900 | 1.09 | 9265 | 55369-6417 | USA | N30 | 2172 | Nucor Insulated Panel Group LLC | 75067 | 343071 | 1148P.NPW¦ 1/4" - 14 x 6" HWH Type 3 SDS w/BN washer¦BRIGHT WHITE | PUR | 1148P.NPW¦ 1/4" - 14 x 6" HWH Type 3 SDS w/BN washer¦BRIGHT WHITE | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-10-19T00:00:00
135520 | 2 | 5 | States | Dayton | Robert Boulka | TRUE | 2026-08-17T00:00:00 | 2026-10-12T00:00:00 | 2026-10-12T00:00:00 | 1500 | 0 | 1500 | 1.09 | 9265 | 55369-6417 | USA | N30 | 2172 | Nucor Insulated Panel Group LLC | 75067 | 343071 | 1148P.NPW¦ 1/4" - 14 x 6" HWH Type 3 SDS w/BN washer¦BRIGHT WHITE | PUR | 1148P.NPW¦ 1/4" - 14 x 6" HWH Type 3 SDS w/BN washer¦BRIGHT WHITE | EA | EA |  | TRUE |  | P | PPD | DAYTON | 2026-11-09T00:00:00
136063 | 2 | 6 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 7 | 0 | 7 | 327.79 | 22289.72 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-7
136063 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 1 | 0 | 1 | 116.25 | 7905 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-2
136063 | 2 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 7 | 0 | 7 | 327.79 | 22289.72 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-4
136063 | 2 | 5 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 7 | 0 | 7 | 327.79 | 22289.72 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-6
136063 | 1 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 7 | 0 | 7 | 116.25 | 7905 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-4
136063 | 2 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 4 | 0 | 4 | 327.79 | 22289.72 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-3
136063 | 2 | 4 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 7 | 0 | 7 | 327.79 | 22289.72 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-5
136063 | 1 | 4 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 7 | 0 | 7 | 116.25 | 7905 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-5
136063 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 1 | 0 | 1 | 327.79 | 22289.72 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-2
136063 | 1 | 5 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 7 | 0 | 7 | 116.25 | 7905 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-6
136063 | 1 | 8 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-12-23T00:00:00 |  | 34 | 0 | 34 | 116.25 | 7905 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-1-2
136063 | 2 | 8 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-12-28T00:00:00 |  | 34 | 0 | 34 | 327.79 | 22289.72 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-1-2
136063 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 4 | 0 | 4 | 116.25 | 7905 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-3
136063 | 2 | 7 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 1 | 0 | 1 | 327.79 | 22289.72 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-1
136063 | 1 | 6 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 7 | 0 | 7 | 116.25 | 7905 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-7
136063 | 1 | 7 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-14T00:00:00 |  | 1 | 0 | 1 | 116.25 | 7905 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-1
136066 | 1 | 4 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-10-02T00:00:00 |  | 1 | 0 | 1 | 3952.5 | 15810 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | MDC Relay PFDD | MDC Relay Protection Functional Design Document | PUR | MDC Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77359-4-1
136066 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-10-02T00:00:00 |  | 1 | 0 | 1 | 3952.5 | 15810 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | MDC Relay PFDD | MDC Relay Protection Functional Design Document | PUR | MDC Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77359-2-1
136066 | 2 | 4 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-10-16T00:00:00 |  | 1 | 0 | 1 | 5100 | 20400 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | MDC Relay SP | MDC Relay Settings Package (4 lineups / 24 devices) | PUR | MDC Relay Settings Package (4 lineups / 24 devices) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77359-4-1
136066 | 2 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-10-16T00:00:00 |  | 1 | 0 | 1 | 5100 | 20400 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | MDC Relay SP | MDC Relay Settings Package (4 lineups / 24 devices) | PUR | MDC Relay Settings Package (4 lineups / 24 devices) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77359-2-1
136066 | 2 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-10-16T00:00:00 |  | 1 | 0 | 1 | 5100 | 20400 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | MDC Relay SP | MDC Relay Settings Package (4 lineups / 24 devices) | PUR | MDC Relay Settings Package (4 lineups / 24 devices) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77359-3-1
136066 | 1 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-10-02T00:00:00 |  | 1 | 0 | 1 | 3952.5 | 15810 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | MDC Relay PFDD | MDC Relay Protection Functional Design Document | PUR | MDC Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77359-3-1
136066 | 3 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-09-25T00:00:00 |  | 8 | 0 | 8 | 1534.38 | 12275.04 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | SDC Relay PFDD | SDC Relay Protection Functional Design Document | PUR | SDC Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77359-6-1
136066 | 4 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-10-09T00:00:00 |  | 8 | 0 | 8 | 1672.5 | 13380 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | SDC Relay SP | SDC Relay Settings Package (8 lineups / 32 relays) | PUR | SDC Relay Settings Package (8 lineups / 32 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77359-6-1
136066 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-10-02T00:00:00 |  | 1 | 0 | 1 | 3952.5 | 15810 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | MDC Relay PFDD | MDC Relay Protection Functional Design Document | PUR | MDC Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77359-1-1
136066 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-14T00:00:00 | 2026-10-16T00:00:00 |  | 1 | 0 | 1 | 5100 | 20400 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | MDC Relay SP | MDC Relay Settings Package (4 lineups / 24 devices) | PUR | MDC Relay Settings Package (4 lineups / 24 devices) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77359-1-1
136157 | 2 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-09-16T00:00:00 | 2026-10-20T00:00:00 |  | 4 | 0 | 4 | 327.79 | 3933.48 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-9
136157 | 2 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-09-16T00:00:00 | 2026-10-27T00:00:00 |  | 4 | 0 | 4 | 327.79 | 3933.48 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-10
136157 | 2 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-16T00:00:00 | 2026-10-13T00:00:00 |  | 4 | 0 | 4 | 327.79 | 3933.48 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay SP | RMU Relay Settings Package (68 RUMs / 68 relays) | PUR | RMU Relay Settings Package (68 RUMs / 68 relays) | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-8
136157 | 1 | 3 | States | Dayton | Andrew Olson | TRUE | 2026-09-16T00:00:00 | 2026-10-23T00:00:00 |  | 4 | 0 | 4 | 116.25 | 1395 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-10
136157 | 1 | 1 | States | Dayton | Andrew Olson | TRUE | 2026-09-16T00:00:00 | 2026-10-09T00:00:00 |  | 4 | 0 | 4 | 116.25 | 1395 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-8
136157 | 1 | 2 | States | Dayton | Andrew Olson | TRUE | 2026-09-16T00:00:00 | 2026-10-16T00:00:00 |  | 4 | 0 | 4 | 116.25 | 1395 | 55369 | USA | N30 | 2178 | Kegan Engineering Group, PLLC | 28227 | RMU Relay PFDD | RMU Relay Protection Functional Design Document | PUR | RMU Relay Protection Functional Design Document | EA | EA |  | FALSE |  | P | PPD | DAYTON |  | 77360-9